# ONTARIO

## ENERGY

BOARD

| FILE NO.: | ### EB - 2007- 0680 |  |
| --- | --- | --- |
| VOLUME: DATE: BEFORE: | 4 December 7, 2007 Paul Sommerville Paul Vlahos David Balsillie | Presiding Member Member Member |

EB-2007-0680

#### THE ONTARIO ENERGY BOARD

IN THE MATTER OF the Ontario Energy Board Act, 1998, S.O. 1998, c.15 (Sched. B);

AND IN THE MATTER OF an application by Toronto Hydro Electric System Limited pursuant to section 78 of the Ontario Energy Board Act, 1998 for an order approving just and reasonable distribution rates and other charges for electricity distribution to be effective May 1, 2008.

Hearing held at 2300 Yonge Street,

25th Floor, Toronto, Ontario, on Friday,

December 7, 2007, commencing at 9:31 a.m.

------------

VOLUME 4

------------

B E F O R E:

PAUL SOMMERVILLE		PRESIDING MEMBER

PAUL VLAHOS			MEMBER

DAVID BALSILLIE		MEMBER

A P P E A R A N C E S

PETER FAYE			Board Counsel

CHRISTIE CLARK		Board Staff

KEITH RITCHIE

SILVAN CHEUNG

MARTIN BENUM

MARK RODGER			Toronto Hydro-Electric System Limited

GLEN WINN

COLIN MCCLORG

COLLEEN RICHMOND

JACK LENARTOWICZ

BASIL ALEXANDER		Pollution Probe

MURRAY KLIPPENSTEIN

ROBERT WARREN		Consumers Council of Canada

JULIE GIRVAN

MICHAEL BUONAGURO 		Vulnerable Energy Consumers Coalition

JOHN DeVELLIS		School Energy Coalition

KIMBLE F. AINSLIE		Energy Probe

DAVID MACINTOSH

I N D E X   O F   P R O C E E D I N G S

Description						    	   Page No.

--- Upon commencing at 9:31 a.m.					1

PRELIMINARY MATTERS								1

THESL - Panel 3: CONTINUED						3

IVANO LABRICCIOSA; Previously sworn.

ASHEEF JAMAL; Previously sworn.

ROBERT WONG; Previously sworn.

EDUARDO BRESANI; Previously sworn.

SUSAN DAVIDSON; Previously sworn.

CROSS-EXAMINATION BY MR. KLIPPENSTEIN				4

CROSS-EXAMINATION BY MR. DeVELLIS				    41

--- Recess taken at 11:00 a.m.				    51

--- On resuming at 11:20 a.m.					    51

CROSS-EXAMINATION BY MR. FAYE					    58

--- Luncheon recess taken at 11:51 a.m.			    67

--- On resuming at 1:31 p.m.					    67

PRELIMINARY MATTERS							    68

CROSS-EXAMINATION BY MR. BUONAGURO				    70

QUESTIONS BY THE BOARD						    72

QUESTIONS BY BOARD STAFF						    81

CROSS-EXAMINATION BY MR. FAYE (Continued)		    86

--- Recess taken at 2:59 p.m.					   121

--- On resuming at 3:18 p.m.					   121

--- Whereupon the hearing adjourned at 4:46 p.m.	   173

E X H I B I T S

Description					  Page No.

EXHIBIT NO. 4.1:  DOCUMENT REFERENCE BOOK OF POLLUTION PROBE.						 3

EXHIBIT NO. 4.2:  INTERROGATORY 10 AND RESPONSE OF POLLUTION PROBE.						 3

U N D E R T A K I N G S

Description						Page No.

UNDERTAKING NO. T4.1:  HOW THE CALCULATION FOR RETURN ON EQUITY WAS DONE.								86

Friday, December 7, 2007

--- Upon commencing at 9:31 a.m.

MR. SOMMERVILLE:  Good morning.  Please be seated.

This is Day 4 of the oral evidence in the matter of an application for rates, made by the Toronto Hydro-Electric System Limited.  It has been designated EB-2007-0680.

Mr. Rodger, are there any preliminary matters?

PRELIMINARY MATTERS:

MR. RODGER:  Good morning, Mr. Chairman.  Just a couple of matters.  I've handed to Mr. Faye to be handed to the Board some responses to undertakings that were given.  In particular, you will receive shortly a copy of Undertaking Response T3.3, T3.4, and T3.7.  And then, additionally, there is a blue page, which is an update to a response to an Ontario Energy Board Staff interrogatory.

And just to explain this blue page quickly, Board Staff's interrogatory had to do with incremental OPEX changes as a result of Smart Meters, and the table that was provided in the interrogatory answer was created specifically to address the Board staff's issue, but Ms. Davidson has discovered that there was an Excel spreadsheet duplication of some of the numbers, which have been corrected here.

Now, there is no impact on the distribution revenue expenses used in the application.  The change only affects the answer to this interrogatory, and nothing else in the application.  But Ms. Davidson did want to update the interrogatory response to reflect the change.

And those are the preliminary matters, sir.

MR. SOMMERVILLE:  Thank you.

Now, we left off with -- Mr. Warren had -- are there preliminary matters from any other party this morning?

Mr. Warren had left off.  Who is next in line?

MR. KLIPPENSTEIN:  Good morning, Mr. Chairman.  I believe I am.  Murray Klippenstein for Pollution Probe.

MR. SOMMERVILLE:  Thank you, Mr. Klippenstein.  Are you ready to proceed?

MR. KLIPPENSTEIN:  Yes, I am.

MR. SOMMERVILLE:  Thank you.

MR. KLIPPENSTEIN:  Mr. Chairman and members of the Panel, for convenience, or hopefully for convenience, I on behalf of Pollution Probe have prepared a cross-examination reference book, a copy of which should be before you, and which we distributed to my friend, Mr. Rodger, a while ago, and copies are available here for anyone who we missed in the distribution.

And in addition, there is one document, which is Pollution Probe Interrogatory 10, and the response, which we weren't able to get into the book.

So if those two documents are available to the Panel, that would perhaps be convenient.  And I understand my friend does not have any objection to that document reference book being made an exhibit, and that might be the convenient --

MR. SOMMERVILLE:  Mr. Faye?

MR. FAYE:  It's Exhibit 4.1.

EXHIBIT NO. 4.1:  DOCUMENT REFERENCE BOOK OF POLLUTION PROBE.

MR. SOMMERVILLE:  And should we make the interrogatory a separate exhibit, or do you want to just consider it part of the --

MR. FAYE:  Maybe for convenience, it would be useful to have it separate.

MR. SOMMERVILLE:  Thank you.

MR. FAYE:  Make that 4.2.

MR. SOMMERVILLE:  Thank you.

EXHIBIT NO. 4.2:  INTERROGATORY 10 AND RESPONSE OF POLLUTION PROBE.

MR. SOMMERVILLE:  Let me say, Mr. Klippenstein, that this kind of booklet is extremely helpful to the Board.  Thank you.

MR. KLIPPENSTEIN:  It may be too early to say that, but --

MR. SOMMERVILLE:  I may have to eat those words later, but it's early in the day, and I'm looking on the bright side.

MR. KLIPPENSTEIN:  Thank you.  I hoped it would be helpful.

THESL - Panel 3:

IVANO LABRICCIOSA; Previously sworn.

ASHEEF JAMAL; Previously sworn.

ROBERT WONG; Previously sworn.

EDUARDO BRESANI; Previously sworn.

SUSAN DAVIDSON; Previously sworn.

CROSS-EXAMINATION BY MR. KLIPPENSTEIN:

MR. KLIPPENSTEIN:  Good morning, members of the witness panel.  My name is Murray Klippenstein.  I'm representing Pollution Probe here, and I would like to ask you a number of questions for a while about the plan we are considering in this hearing.

Pollution Probe would like to test whether the plan from Toronto Hydro to meet its customers' electricity service needs is economically prudent and cost-effective.

And as part of that, I would want to be asking questions directed to whether Toronto Hydro's customers' electricity needs could be met in a more prudent and more cost-effective manner if there was more in the plan about energy conservation and small-scale local generation, or what I'll loosely call distributed generation.

So I'm going to be asking a lot about energy conservation and distributed generation, and I guess the obvious context is that what Toronto Hydro is seeking here is OEB approval for a three-year, $900-million capital plan.  Have I got that obvious point right so far?

MR. LABRICCIOSA:  That's correct, sir.

MR. KLIPPENSTEIN:  Good.  I'd like to start by asking you to turn in the document reference book, Exhibit 4.1, to Tab 4, and this appears to be a letter from David S. O'Brien, dated July 13th, 2007, on behalf of Toronto Hydro Corporation.  Does that make sense so far?

MR. LABRICCIOSA:  Yes, sir.

MR. KLIPPENSTEIN:  And Toronto Hydro Corporation is the sole shareholder of Toronto Hydro-Electric Services Limited, or Toronto Hydro; is that right?

MR. LABRICCIOSA:  The City is the shareholder.  Toronto Hydro Corporation is the parent corp. company.

MR. KLIPPENSTEIN:  Okay.  Thanks.

And the letter is addressed to Councillor Paula Fletcher, of the City, I guess; right, it would appear?

MR. LABRICCIOSA:  Yes, sir.

MR. KLIPPENSTEIN:  I'd like to refer to several sentences in this letter for beginning my cross-examination about the topics I mentioned.  I'll read the first two sentences.  And some of it is kind of fluff, but just to make sure the context there isn't misunderstood:

"Further to our conversation yesterday regarding the information released by Toronto Hydro at a meeting on July 10th, I want to state emphatically that neither Toronto Hydro nor Hydro One is pursuing any option, such as the so-called third line, as the preferred solution to the security of supply issues facing this City.  Minister Duncan has made it very clear that the government does not support the third line as an option, and we support that opinion."

Now, just by way of background, the reference to the "third line", just so I can make sure I understand this, in very simple terms, I take it that there are basically two major transmission lines coming into and serving the general downtown Toronto core, one of which ends at Leaside station, and one ends at Manby station; is that right?

MR. LABRICCIOSA:  That's correct, sir.

MR. KLIPPENSTEIN:  And so the "third line" referred to here is the idea of a third major transmission line to serve -- or to additionally serve, basically, the downtown Toronto area generally.  Is that generally right?

MR. LABRICCIOSA:  Yes, sir.

MR. KLIPPENSTEIN:  Okay, and just following up on that, the two transmission lines that I mentioned which end at Leaside and Manby, Toronto Hydro's distribution system picks up on the other side of those two stations and distributes the power basically from there to the downtown Toronto area.  Is that roughly right?

MR. LABRICCIOSA:  It's a bit more complex than that, but I guess in simple terms, if you look at it as two extension cords that have nodes connected from it -- I mean, there are many transmission stations throughout the city, 35, in fact, that pick up -- that are pick-up points, essentially, from there that we feed the customers of Toronto.

So, you know, essentially they come off two main trunks, which end at Leaside and Manby.  So, you know, your point is relatively correct in terms of the two trunks feed those 35 pick-up points.

MR. KLIPPENSTEIN:  I see.  And the parts of the system between the two -- Leaside and Manby stations, and then those 35 points that you mentioned -- are those part of Toronto's system or Hydro One's system?

MR. LABRICCIOSA:  With the exception of one transformer station, they're all Ontario -- Hydro One's pick-up points.

MR. KLIPPENSTEIN:  I see.  Okay.  Thank you, that's helpful.

Let me continue with the letter, just skipping over a sentence:

"Unfortunately, a piece of outdated information was included in the presentation which gave the impression that Toronto Hydro and Hydro One were pursuing the third line option.  Nothing could be further from the truth."

Then if I could skip one sentence to the next paragraph:

”The material that has been provided to you by Mr. Gibbons has been taken out of context and it was made very clear by my staff to all in attendance that Toronto Hydro is, first and foremost, committed to seeking demand-side management and distributed generation solutions to the supply concerns that all parties recognize must be addressed."

Now, skipping the first part of that sentence, which refers to Mr. Gibbons, who I am not here today to defend, but just looking at what it says about Toronto Hydro.  It says that Toronto Hydro is:

"-- first and foremost committed to seeking demand-side management and distributed generation solutions."

Would you agree that it would be fair and appropriate for this Board to take this letter and that statement as an appropriate context in which to consider the plan that it's considering in this hearing?

MR. LABRICCIOSA:  I really can't speak for the Board,

Mr. Klippenstein, but I'm trying to understand your question in terms of:  Are you suggesting that the materials submitted do not reflect conservation and demand management?

MR. KLIPPENSTEIN:  Well, we'll get to that, but I want to take it step by step.  My first question is whether you would agree with me, and I'm suggesting to you that it is fair and appropriate for this Board to take that sentence and the rest of the letter, but that sentence, into consideration as context when it evaluates the plan before it.  Would you agree that's fair?

--- Witness panel confers

MR. LABRICCIOSA:  I would agree with you.  I would say conservation demand management is included in this plan, and it is a part of the submission to the Board.

MR. KLIPPENSTEIN:  All right.  And if you turn to the second page of the letter and just look at the cc list, the copy list, I see that this letter was apparently copied to the Honourable Dwight Duncan, the Minister of Energy; the Mayor of Toronto, David Millar, Dr. Jan Carr, the CEO of Ontario Power Authority, and Laura Formusa, the then-acting president and CEO of Hydro One, and I gather she's now the president and CEO.

You would agree with me that this letter has been made as a public statement to many, if not most of the major players in the plan that we're dealing with today?

Is that fair?

MR. LABRICCIOSA:  I would say so.

MR. KLIPPENSTEIN:  Have you become aware of any way in which the author of this letter, the president of Toronto Hydro Corporation, or anyone on behalf, has withdrawn or changed in any way the contents of this letter and the statements therein?

MR. LABRICCIOSA:  I'm not aware of a follow-up letter beyond that.

MR. KLIPPENSTEIN:  And as far as you know, Toronto

Hydro Corporation, through its president, has never backed away from the statements in this letter?

MR. LABRICCIOSA:  Again, I'd just reiterate, outside of this letter I have not seen anything else come out of this.

MR. KLIPPENSTEIN:  I'd like to then change references and look at some of the aspects of the distributed generation issue in the context of that letter.  And if you could turn to Tab 5 of the Pollution Probe document book, Exhibit 4.1.  That's Tab 5 of the document book, which is Pollution Probe Interrogatory No. 6 and Toronto Hydro answers to that.  Do you have that?

MR. LABRICCIOSA:  Yes, I do, sir.

MR. SOMMERVILLE:  Just to clarify matters,

Mr. Klippenstein, the actual exhibit number is S4.1.

MR. KLIPPENSTEIN:  I'm sorry.  Thank you.

MR. SOMMERVILLE:  And similarly, S4.2 for the other.

Thank you.

MR. KLIPPENSTEIN:  The first question asked in that interrogatory at Tab 5 says:

"Please provide your best estimate of the amount of distributed generation in MW that your system can presently accommodate in downtown Toronto."

Now, for the context of this discussion, as I understand it, distributed generation means generation that occurs inside the boundaries of Toronto Hydro's system, roughly, rather than generation that occurs outside and is transmitted in. Fair enough in a general way?

MR. LABRICCIOSA:  In the industry, it's more or less known as a small-scale footprint type generation.  So, you know, the larger footprint, like the Portlands Energy

Centre -- that's a recent one that's being built by OPG -- is not distributed generation, even though it's located within the City of Toronto.

MR. KLIPPENSTEIN:  Okay.  I'll get to the larger-scale ones, later, but in general it would include instances of the large buildings, or users that create their own generation capacity that's within Toronto Hydro's jurisdictional area, within your system; right?

MR. LABRICCIOSA:  I would agree with that.

MR. KLIPPENSTEIN:  And would that include things like a large shopping mall, like perhaps Eaton Centre or a condominium building or some kind of commercial establishment, or even an apartment building or even a home?  Those would all potentially be examples of distributed generation.

MR. LABRICCIOSA:  We have many examples today where that's working in our system, correct.

MR. KLIPPENSTEIN:  What we asked for in the interrogatory was your best estimate of the amount of distributed generation that your system can presently accommodate in downtown Toronto.  Part of the answer is found on the next page, which is at page 9 of the document book.  And it says: "Based on a preliminary..."  Do you see that?

MR. LABRICCIOSA:  I do.

MR. KLIPPENSTEIN:  (Reading.)

"Based on a preliminary and high-level review, THESL indicated that there may be room for up to 300 MW of DG" -- I guess that's distributed generation – "in sizes of less than 10 megawatts in the combined Leaside and Manby systems.  It is assumed that with appropriate planning and design for this level of penetration, the form and function of the distribution system would not be altered.  That is, the distribution system currently designed, built, operated and protected as a unidirectional power system would be maintained and the installation of a generation would not impose restrictions on the ability of the distribution system to connect new or serve existing customers."

And just stopping there in the quote, let me connect this back to the letter that I reviewed with you.  Is it fair to say that, in the letter from Mr. O'Brien, when he talks about Toronto Hydro's commitment to distributed generation solutions, and the quote in the interrogatory I just read, we're talking partly about the same thing there.  Is that right?  It's distributed generation?

MR. LABRICCIOSA:  Yes.

MR. KLIPPENSTEIN:  Yes.  Now, returning to the answer in the interrogatory, one of the words I notice is "unidirectional." It says:

"The distribution system currently designed, built, and operated and protected as a unidirectional power system..."

Am I right in understanding that means that the distributed generation we're talking about in that sentence refers to power generation units which would supply the needs of the particular building but would not feed into Toronto Hydro's grid?  Is that what's meant by "unidirectional?"

MR. LABRICCIOSA:  That's what's meant by "unidirectional", but in essence, I think the term "unidirectional" in that sentence is really used to identify the system is actually built to supply power in one direction.

The fact that it can accommodate bidirectional feeds is a byproduct of the design we have.  I think later on it's hinting at there are some restrictions because of the design, both from a unidirectional perspective as well as short-circuit capacity, that limits the amount of distributed generation you can connect up to the grid.

MR. KLIPPENSTEIN:  Okay.  I'm a little confused, then, and I'd like to just ask for some clarification on that.

The amounts referred to in this question, the 300 megawatts, does that include some sources which in your mind would feed into Toronto Hydro's system in addition to supplying the needs of the particular institution?

MR. LABRICCIOSA:  Well, let's come back to the 300 megawatts.  I think, you know, I want to make sure we're not taking the words that are on the page out of context.

300 megawatts was an assumption, or a number put together based on an assumption from some technical documents delivered out of the U.S., that basically suggests there -- in most urban centres there's about 10 percent of the load is available in distributed generation format.

So I don't want to leave the impression that this 300 megawatts is accounted for in discrete elements out in the system.  It's based on that high-level notional conclusion drawn from two studies out of the States.

MR. KLIPPENSTEIN:  Well, I do want to ask some questions about that some more.  But before I do, let me just understand the words "unidirectional power system".  Maybe it's not as important as I think.

Are you saying that the 300 megawatts -- I understand it's rough -- the 300 megawatts does include some units feeding back into the system, or is it -- sorry?

MR. LABRICCIOSA:  Again, you know, we didn't identify

300 customers with 1-megawatt generators, so whether it can or can't, I can't say with certainty that it's out there.

But I think, if your question's really hinting at, could there be some that feed into the grid, yes, I would imagine there's probably some that's there that could qualify with that statement.

MR. KLIPPENSTEIN:  Does your estimate in that paragraph -- well, let me rephrase that.

I assume that there are some technical issues when you install a distributed generation plant that is going to feed back into the system?

MR. LABRICCIOSA:  Yes, there are.

MR. KLIPPENSTEIN:  Now, in this estimate, are you making the assumption that your present system can accommodate that?  I'll bet it's not that simple.

MR. LABRICCIOSA:  No, it's not that simple.

MR. KLIPPENSTEIN:  Okay.  So when you talk about this 300-megawatt figure, you're not really sure how much of that, if any, would be bidirectional?

MR. LABRICCIOSA:  Correct.  You know, I can also describe our experiences in this area.  Most of the distributed generation that we have connected today just offsets the load of that building.

So, for example, you mentioned, you know, one example you used was the Eaton Centre, and it's a commercial building.  A typical centre like that may be 10 megawatts worth of load.  It may have 1 megawatt worth of distributed generation to be connected.  So essentially, it offsets its own load rather than feeding into the grid.

So most of our connections today are pretty much offsetting load connections, rather than bidirectional connections.

MR. KLIPPENSTEIN:  Okay.  Now, when I look at this answer to the question, I have to say, you know, speaking as a lawyer using technical, legal language, I see a lot of weasel words in there, frankly.  I see the words:

"-- based on a preliminary and high-level review, indicated that there may be room for up to 300 megawatts, and it is assumed that the form and function of the system would not be altered".

That's a lot of weasel words in there, if I may say so.

MR. LABRICCIOSA:  I object to your terminology of "weasel", but I would say that's technical people writing to be certain about not leaving false impressions out there.

MR. KLIPPENSTEIN:  Okay.  Well, as you can see, you didn't leave any false impressions with me.

MR. LABRICCIOSA:  I'd also come back to the interrogatory that said "your best estimate."

MR. KLIPPENSTEIN:  Okay.

MR. LABRICCIOSA:  So again, the impression we're trying to leave here is, there's an estimate.  We've done our best with a lot of assumptions in there.

MR. KLIPPENSTEIN:  Oh, so it's now our fault that you--

MR. LABRICCIOSA:  It may be a weasel word then.

MR. KLIPPENSTEIN:  But anyway, my concern about that is, I see what is a very loose estimate, and you say this was based on basically two studies from the US.

MR. LABRICCIOSA:  I'm going back to my experience with our distributed generation portfolio, and at that time we reviewed two key studies out of New York State and, I believe, California that suggested as an approximation to understand how much capability is out there, the 10 percent rule is a general rule of thumb that's out there.

MR. KLIPPENSTEIN:  All right.  Well, I'm going to suggest that I see a bit of a gap.  In fact, I see a large gap between, on the one hand, this statement from the president of Toronto Hydro that Toronto Hydro is "first and foremost and is committed to seeking distributed generation solutions" and, on the other hand, this statement, which, frankly, is very general, and it's based on two studies from the U.S.  It's based on a rule of thumb.

I take it you haven't actually prepared a listing of possible sites.  And to me that doesn't look like a commitment to -- or a seeking, or that it's a first and foremost priority.  I don't know.

MR. LABRICCIOSA:  I disagree with you, and I'd offer to submit maybe some supporting evidence to try and convince you that we are first and foremost committed to conservation.

A couple of points that I would submit to you:  Just recently we received an international award for our conservation program.  And in fact, it's our peak-saver program, where it is load curtailment, and that international award recognizes Toronto Hydro as having a high energy-efficiency program and a very high market success rate, again, globally, and that stems from our efforts in conservation.

The other element that I would subscribe to you is in, again, our conservation demand management program, under the DG portfolio, I believe we were, out of all the utilities participating, we were the utility with the greatest success of connected megawatts in DG under that program.

So I would say our history and track record has been pretty good, in terms of being a leader in conservation and including distributed generation.

MR. KLIPPENSTEIN:  Well, I can tell you I've won some awards, some of which are pretty dodgy, but -- and the peak-saver is -- you know, when I first heard about your results, I was delighted.  I must say I was just totally impressed.

But, you know, this is a slightly different question we're dealing with here.  And so my focus is at a finer grain, and it's on, you know, on the one hand, this statement.

And this statement was made to all the public political leaders and to the public.  It left an impression of an enormous commitment, and yet what I see here is generalities and a rule of thumb from two U.S. studies.

I mean, do you actually have -- did anybody make a list of possible offsetting distributed generation sites in your system?

MR. LABRICCIOSA:  We do have a list of generation connected to the system.  And that list also includes those that are interested in connected.

MR. KLIPPENSTEIN:  So when you say you have a list of people connected, what do you mean, presently existing distributed generation?

MR. LABRICCIOSA:  That's correct, sir, and I think our -- we have a process to connect generators to the system, so in other words, you know, we invite applicants to come forward.  We work with applicants in developing a plan to connect to the grid.

And it is a process, it is an application, so some people apply, and we don't hear from them.  Some people apply and would like a little effort on our part to help sort through how to connect up, but they still don't connect, I mean, so we work through that.

So there are different people at different stages in the process of connecting generation to the grid, but it is based on an application process.

MR. KLIPPENSTEIN:  You are the folks who know the system more than anyone else, and I would think you have experience and theoretical knowledge and access to information from systems all over the world.

You could actually be a little more proactive and identify lots of specific sites and contact those people with proposals.  Have you done that?

MR. LABRICCIOSA:  It's not that I'm confused by your question.  I mean, we have 700,000 customers in our system.

MR. KLIPPENSTEIN:  Exactly.

MR. LABRICCIOSA:  I guess our reach program is really driven through a couple of channels, one being our Web-based site.  We have a DG section where you can connect up to and get additional information as well as download our connection agreements and requirements to connect.

Under the CDM program, we visited many establishments of possible sites to try and stimulate some interest.  We've also presented through various forums the offerings of our program and how it works and what the process is to connect up to the grid.  So, I would say we did canvass many people, and we did outreach into the public sector to try and get that happening.

MR. KLIPPENSTEIN:  But you know who are good candidates, and you know what are the big buildings and what new buildings are coming up.  Did you go and talk to them?  You are the folks who can say:  This is how it works and here's three options.  But you haven't done that, I take it?

MR. LABRICCIOSA:  Well, we do have key account reps that talk to the large customer class, so that the ones that you're referencing, we do have people that have that conversation.

Again, I'm going to remind you as well, you know, it is voluntary from the perspective of the customer has to want to do this.  They own the generation, and if they should decide not to, I mean, I don't think we can force them to do it.  It is their choice.

MR. KLIPPENSTEIN:  You didn't include any of the information about your outreach program in the evidence for this application, I take it?

MR. LABRICCIOSA:  No, the question that was asked was provide a best estimate, if you're referring to the interrogatory, and again, it was trying to be an all-encompassing type question with an all-encompassing type answer to say this is what is possible.

I guess we could have narrowly answered the question by saying:  This is what we know.

MR. KLIPPENSTEIN:  Now, what about bidirectional distributed generation?  Do you have any estimate or assessment of bidirectional opportunities in your system for distributed generation?

MR. LABRICCIOSA:  Again, if you're asking for an estimate, we could put the language back in that

I guess you don't really like.  But I would say we have some today.  We have some that are connected and we're aware of it.  We have some that have applied but have not taken it any further that we know of.  And then we have -- I'm sure there are units out there we don't know of that can be bidirectional.

MR. KLIPPENSTEIN:  Well, one reason why I'm asking these questions is because we're here to look at a capital plan today, and I would assume, in my ignorance, that if you foresaw an aggressive uptake of distributed generation, whether it's unidirectional or bidirectional, you would have to consider what kind of technical investments or changes you would have to take to your system.  Is that fair?

MR. LABRICCIOSA:  We would have to definitely take that into account, sure.  I mean, we do that as part of our regular process today.

MR. KLIPPENSTEIN:  And have you done some estimate of what technical capital planning requirements would arise from aggressive distributed generation, unidirectional and bidirectional?

MR. LABRICCIOSA:  For distributed generation units that have to connect up to the grid that want to be bidirectional, our connection agreement states that they are responsible for the costs and the upgrades that are responsible to make it bidirectional.

So from a capital planning perspective, if your question is have we accounted for that in our plan, again, I'm going to maybe give you a bit of a complex answer.

Our plan today is based on the Market Rules that we know of today, which has a small uptake of distributed generation, some.  And we've already factored that in.

So we don't expect, unless the rules change, a huge flow of connections coming forward.

Having said that, if it does happen, along your point of, you know, should it go forward, what would we do, we would follow our connection agreement, which basically puts the onus back on the customer who wants to connect up to the grid, and not put that burden on the rest of the rate base.

MR. KLIPPENSTEIN:  So your present assumption is that if somebody wants to do a major distributed generation project, it's their problem to deal with and pay for the technical upgrades that are required.

MR. LABRICCIOSA:  I wouldn't necessarily say it's their problem.  I would say we have a process that we work with them in helping to put some solutions in place that will work.

The financial burden, of course, resides with them if there are major implications on the grid.

MR. KLIPPENSTEIN:  Well, I have to say again, I really question whether that is the kind of commitment that merits the public statement that the president made.  You're telling me that you don't really expect a huge flow.  It's sort of up to the clients, or whatever you want to call them; that they're responsible for the costs and the technical stuff to some degree.

This is a formula for not much happening.

MR. LABRICCIOSA:  I mean, the policy is what it is, and it really is a policy-type statement I think you're making, reflective of, if the market doesn't bear fruit it's a function of the policies and structure of the marketplace.

MR. KLIPPENSTEIN:  Let me ask a more specific question about small-scale distributed generation; let me say 40 MW or less as a cutoff point.

MR. LABRICCIOSA:  We generally use 10 MW or less, but I mean, let's go with your 40, and we'll see how the question plays out.

MR. KLIPPENSTEIN:  What is your best estimate of the quantity of that size of distributed generation site that could be embedded into your distribution system with the status quo, the given infrastructure.

MR. LABRICCIOSA:  Forty is a good number from your perspective.  It's a very complex answer.

When you look at the grid, for example, a feeder that supplies consumers generally handles 20 MW.  So at 10 MW or less, you really can handle two or more connections at the feeder level.

Once you exceed 20, you now have to connect up to the transformer station level, which is really outside of that feeder at the bus level, which is almost connected up to the transmission system.  It still can be connected up to the bus, but, depending on technical issues at the station level, it could require you to connect up to the high-voltage level.

So 40, I guess, in that example is a bit of a complex borderline issue.

MR. KLIPPENSTEIN:  But to go back to my question, do you have an estimate, or what would be your best estimate or what would be, given what you've said, of how many 40- megawatt or less facilities you could embed?

MR. LABRICCIOSA:  I don't have that estimate, and I really don't know how many exist out there.

MR. KLIPPENSTEIN:  Is that something you could produce, an estimate of how many up-to-40 megawatt facilities could be embedded with the status quo infrastructure?

MR. LABRICCIOSA:  I would say the answer would be, we don't have any.  So I could produce a list that says nothing.  And I'm struggling a little bit with the answer, because you keep saying 40 megawatts.  And as far as I know, there are none in Toronto of that size that are connected to our grid, subject to check -- go back into our databases and ask, you know, people downstream in the organization to scour all the connection files.

MR. KLIPPENSTEIN:  That's partly my point, is it's partly about potential, I think.  I mean, do you know -- that was my question -- how many could be connected up of that size?

MR. LABRICCIOSA:  No.  Sorry, I wouldn't know how to frame up that estimate.

MR. KLIPPENSTEIN:  You haven't done it for purposes of this plan, obviously?

MR. LABRICCIOSA:  No.

MR. KLIPPENSTEIN:  So if this Board were looking at distributed generation in terms of a capital plan and as part of the solution to the supply concerns that all parties recognize must be addressed, to quote the president, you don't have any answer as to how many of those 40-megawatt or less facilities could be embedded?  You just don't know?

MR. LABRICCIOSA:  I would say, based on what we know today, none.

MR. KLIPPENSTEIN:  And in the capital budget as proposed, will it increase the capacity of the system to accept such facilities in the future in downtown Toronto?

MR. LABRICCIOSA:  We're not designing it for that size and scale of unit at this time.

MR. KLIPPENSTEIN:  Isn't that a bit of a problem?  Don't you think you should be?

MR. LABRICCIOSA:  There are none that we know of today.

MR. KLIPPENSTEIN:  And you haven't really looked, though, have you?

MR. LABRICCIOSA:  Well, in our efforts to look, nothing has come up.

MR. KLIPPENSTEIN:  So what we can take from your evidence, what the Board can take, is that the capital plan and budget as proposed, if it was approved, really does not in any way address the potential distributed generation sites of up to 40 megawatts that might be out there for the future.

MR. LABRICCIOSA:  Well, up to --

MR. KLIPPENSTEIN:  Up to 10.

MR. LABRICCIOSA:  Up to 10, yes, I think we, you know, we do have some connections in play today.  You asked at 40 megawatts.  At that discrete level, that discrete number, we have none that exist today.

Could one come forward?  I guess it's possible.  I would come back to the CDM section in our capital plan that identifies the amount of effort and investment we have in CDM, which would include those -- you know, which would include DG effort, and would incent, you know, generation that we're familiar with today to come to the grid.

MR. KLIPPENSTEIN:  All right.  Let me ask about this in the context of the third line.  About how many megawatts of smaller-scale distributed generation would need to be embedded into your system in downtown Toronto to avoid the need for the third line?

MR. LABRICCIOSA:  The 300-megawatt number really speaks to that issue.  So if your question is, well, how many 1-megawatt generators do you need to get to 300, it would be 300, or 150 2-megawatt or, you know, 30 10-megawatt.  Any combination would do.

MR. KLIPPENSTEIN:  But if, you know, the third line was raised as a way to get more power into downtown Toronto, distributed generation is a way of avoiding the third line, because you're generating the power or you're offsetting the power right within Toronto.

And so how many megawatts -- are you telling me that you will need 300 megawatts of small-scale distributed generation within Toronto to avoid the third line?

MR. LABRICCIOSA:  I can't really comment on the third line, whether it avoids it or not, at this stage.  But the issue stems from the fact that, should a contingency happen in the City of Toronto, we would not have 300 megawatts of available capacity in the grid today the way it exists, to deal with that -- with that outage, that first contingency situation.

So whether it avoids the third line, there are a whole host of issues around that third line that I think Hydro One can speak of from a technical perspective in support of that solution, beyond just this contingency issue.

So, you know, your question comes back to, if you had 300 megawatts, you can avoid it altogether?  I can't really comment on avoiding that solution.  I can comment on the impact of not having that solution or any other solutions on the City of Toronto.  And it would be 300 megawatts of power outages in the system.

MR. KLIPPENSTEIN:  Well, if I understand your answer -- I'm not sure I do -- but if I understand your answer, it seems to me your plan should be looking at how to facilitate or incentivize or stimulate or plan for 300 megawatts of distributed generation in Toronto from a technical and financial point of view; isn't that right?

MR. LABRICCIOSA:  And I would say it does.  With the CDM program, it's aimed at trying to stimulate as much conservation or supply that we can get at this stage.

I would also suggest to you -- again, you keep coming back to the context of the third supply.  In our filing it's nowhere to be found, in terms of evidence or solutions or contribution.  And it's not within our jurisdiction to promote or not promote that solution from that perspective.  That's really a Hydro One system responsibility.

And again, from what I know in working with Hydro One, there are a whole host of issues outside of just the shortage of supply that that solution is trying to address as well.

MR. KLIPPENSTEIN:  If I was going to ask for a description of the technical aspects of the system that are presently in this budget that will accommodate expanded distributed generation, what would I look for?  Do you have any such examination or study?

MR. LABRICCIOSA:  Again, if I understand your question correctly, when you -- we don't know of any single 40-megawatt generation sources that are going to come forward.

However, the impact of any generation, regardless of the size, is reconfiguration of the system, both from a protection-scheme perspective -- that's one element, in terms of providing protection downstream, and protection coordination.

When you do that, we have things like electronic relaying versus electromechanical relaying.  This program that we put in front of you, when you look at the circuit breaker replacement and switch-gear replacement programs, deals with converting electromechanical to electronic type relaying.

--- Reporter appeals.

MR. LABRICCIOSA:  Sorry, electromechanical versus electronic relaying.

So from that perspective, you know, there are elements of these investments we're making today that would facilitate not only small-scale generation, but most generation that would exist.  In essence, we would have to reprogram the protection setting rather than replace it.

So that's an example I bring forward that's included in this plan.

MR. KLIPPENSTEIN:  And that's an example, but do you have at all an overall strategy?  You've mentioned one example.  There must be other technical requirements of a, let's say, a 30-megawatt bidirectional distributed generation.

MR. LABRICCIOSA:  It's a rarity in the system today, so, you know, our program is really addressed at reliability of the system and replacing aging assets and infrastructure.  That's our focus.

And to the extent that we could design it to accommodate typical generation, we are.  Again, size of conductor, relaying, modernizing the asset, those kinds of elements.  I would suggest to you we're not designing it for the atypical connection.

MR. KLIPPENSTEIN:  And bidirectional would be an atypical connection?

MR. LABRICCIOSA:  No, we do have bidirectional today.  40 megawatts would be atypical.

MR. KLIPPENSTEIN:  Do you have any 30-megawatt?

MR. LABRICCIOSA:  No, sir.

MR. KLIPPENSTEIN:  Any 20?

MR. LABRICCIOSA:  No.

MR. KLIPPENSTEIN:  Any 15?

MR. LABRICCIOSA:  No, we have a 12-megawatt connection.

MR. KLIPPENSTEIN:  How many do you have, let's say, between 10 and 15; do you know?

MR. LABRICCIOSA:  A handful.

MR. KLIPPENSTEIN:  Is your system now ready to accept a 15-megawatt or 20 or 30 or 40-megawatt bidirectional?

MR. LABRICCIOSA:  Again, we classify distributed generation as 10 megawatts or less, and the answer would be yes.  As you're getting closer to 15 and 20, I'd have to say, if you're connecting to the distribution system, no.  It's inherently not designed to carry anything more than 15 to 20 megawatts, so we would not connect it there.

It would have to be an express connection either to one of those 35 delivery points or to the Hydro One transmission system.

MR. KLIPPENSTEIN:  Basically, the system is not capable now, and your plan doesn't make it capable, of any embedded distributed generation above 15 megawatts, and your plan doesn't have any money or planning to deal with that?

MR. LABRICCIOSA:  We've had no applications come in beyond the 12-megawatt that I spoke of.  And I would say we're very much connected with our customers and know what they're doing.

MR. KLIPPENSTEIN:  I take it the answer to my question is no, and I also take it that if such a thing ever is proposed to you or someone, or it dawns upon you that it is possible and is a good idea, the present regime is the customer has to pay for it.

MR. LABRICCIOSA:  In terms of making the connection, that's correct.

MR. KLIPPENSTEIN:  I take it it would be possible for

Toronto Hydro to go back and have another look at its capital plan and say:  Let's try and accommodate distributed generation of 15, 20, 30, 40 megawatts, and do an assessment of what might be required in your capital plan to do that.

MR. LABRICCIOSA:  I would suggest to you that we could not connect it to our grid regardless of how often we looked at it.  I mean, once you get past a certain size, you're connecting upstream, not at the grid level.

So we would have to work with Hydro One and any other stakeholders in the transmission arena that would require that, which would include the IESO, and possibly the OPA as well.

Again, from a technical constraint perspective, 20 is the limit, and it's not necessarily by design to avoid generation, it is in terms of the design of the system and how it feeds the customers today.

MR. KLIPPENSTEIN:  Now, the proposed three-year capital budget is part of a larger ten-year capital budget to meet your customers' electricity needs, correct?

MR. LABRICCIOSA:  It's part of a ten-year plan, that's correct.

MR. KLIPPENSTEIN:  Right.  And what is the dollar value of your ten-year plan?

MR. LABRICCIOSA:  The initial estimate in the submission, I believe, subject to check, would be 1.17 billion, close to 1.2 billion.

MR. KLIPPENSTEIN:  1.17 billion.  Okay.  And I take it that will have some rate impact; in other words, -- sorry, let me clarify.

Not the 10-year budget but the three-year capital budget will have some rate impact; it will cause the rates to rise somewhat.  Is that fair?  The three-year plan is --

MR. LABRICCIOSA:  I think Mr. Haines in his opening remarks had said it's 4 percent over three years in terms of the net impact.

MR. KLIPPENSTEIN:  Okay.   And so you have to watch your level of capital spending in those three years, in 2008, 2009, 2010.  You're somewhat constrained, in other words, because you have to avoid undue rate increases; that constrains your capital budget expenditures?

MR. LABRICCIOSA:  I think if you are asking whether rate fluctuations are a consideration in terms of the plans we put forward, I would say yes.

MR. KLIPPENSTEIN:  And specifically, they constrain your ability to increase capital spending because you have to avoid undue rate increases that might come in?

MR. LABRICCIOSA:  I mean, the investment we put forward is for the system and power delivery, reliable power delivery.  And there is a connection between investment, rate increases, and the reliable grid performance that you're looking for.

So it's all embedded in there together.  There's a balancing point, I would suspect.  If your question is aimed at one or the other, there's a balancing point you have to contend with.

MR. KLIPPENSTEIN:  And so if you were going to later decide to increase your spending in one area, you have to offset by a reduction in another area if you want to maintain the same balance?

MR. LABRICCIOSA:  I would say it's a fair statement.

You would have to consider that.

MR. KLIPPENSTEIN:  I'd like to ask about distribution system losses, changing the focus for a bit.

If you could turn to Tab 6 of the Pollution Probe reference book, which is Exhibit S4.1.  And at subtab A, in your answer to interrogatory, Toronto Hydro lists its total system losses for the period 1998-2006.

And we calculated those as a percentage of the total purchased energy, and you see our calculations there.  And over that period, it averages out to 3 percent; in other words, the annual average distribution losses as a percentage of total electricity purchases is approximately 3 percent.

Take that subject to check?

MR. LABRICCIOSA:  Yes.

MR. KLIPPENSTEIN:  Now, that's the average losses.  Let me focus instead for a moment on losses at the time of the annual system peak, such as a hot summer day.  Would you agree with me that the marginal system losses as a percentage of electricity purchased will be larger than that average 3 percent on a peak day, because system losses will be greater on a peak day as a percentage?

MR. LABRICCIOSA:  It would be 3 percent.  Are you saying the absolute number would be different?  I would probably agree with you, but it's still a percentage.

MR. KLIPPENSTEIN:  At the time of an annual peak, on a summer day, first of all, the system loss will be higher on an absolute level; right?  And do you agree or disagree that, as a percentage, it would be higher?  Or are you saying that at the higher level, the system loss is still at the same rate?  Seems to me it would be higher; I could be wrong.

MR. LABRICCIOSA:  You're causing me to think about the technical criteria on this one.  I mean, the losses range with the square of the current.  So certainly there is a non-linear effect there.

MR. KLIPPENSTEIN:  Right.  So just using that --

MR. LABRICCIOSA:  Sure.

MR. KLIPPENSTEIN:  Whenever I hear -- I'm not a mathematician, but whenever I hear the word "square", I know it's not a linear, it's --

MR. LABRICCIOSA:  You got it.

MR. KLIPPENSTEIN:  It's some other kind of curve.  Which means that at a higher level, as on a peak day, your system losses are now going to be losing at a higher rate, and therefore it will be higher than average?

MR. LABRICCIOSA:  It could be different.  So we're talking the --

MR. KLIPPENSTEIN:  No, no, not "could" be different.  It will be different, right?

MR. LABRICCIOSA:  We're talking the technical stream.  I also think of the non-technical side, the non-technical losses as well.  So diverting power -- do people who divert power consume more during peak periods?  Probably.  So it will be different.  I agree with you.

So if it's an unmetered load, will that have an impact?  Probably.

MR. KLIPPENSTEIN:  Well, let me try and sort this out.

All things being equal, at a higher level of current, the loss is at a higher rate, correct?

MR. LABRICCIOSA:  Correct.

MR. KLIPPENSTEIN:  Okay, so on a peak day, as opposed to an average day, where the current is higher, then, all things being equal, the loss will be at a higher rate.  It necessarily follows, correct?

MR. LABRICCIOSA:  Correct.

MR. KLIPPENSTEIN:  So all the other things being equal, the marginal system losses as a percentage of electricity purchases will be higher than the average, right?  On a peak day?

MR. LABRICCIOSA:  Correct.

MR. KLIPPENSTEIN:  Will the capital plan -- the expenditures in the capital three-year plan, will it reduce that increase?  In other words, will it reduce Toronto Hydro's system losses as a percentage of electricity purchases at a time of system peak?

MR. LABRICCIOSA:  Yes.

MR. KLIPPENSTEIN:  And do you know by about how much?

MR. LABRICCIOSA:  No.

MR. KLIPPENSTEIN:  Do you have any basis for saying "yes"?

MR. LABRICCIOSA:  As we modernize our plant, our designs take into account optimizing the system for operational flexibility and delivery efficiency.  As we buy equipment, newer equipment today, modern equipment has, by design, lower losses.

As we upgrade our system, we do things like voltage conversion.  So we convert from a lower voltage/higher loss level to a higher voltage/lower loss level.  Those are some examples.

MR. KLIPPENSTEIN:  Do you have any estimate or any way of advising us of the cost-effectiveness of those expenditures in reducing distribution losses during the peak hours?

MR. LABRICCIOSA:  No.

MR. KLIPPENSTEIN:  And is there any reason why you don't?

MR. LABRICCIOSA:  We have never been asked.

MR. KLIPPENSTEIN:  And you've never decided that the distribution losses at peak times are worth that kind of look?

MR. LABRICCIOSA:  No.  I think the issue we have in front of us today, the plan we have in front of us, deals with reliability, not necessarily focused around load losses.  Load-loss improvement is really a byproduct of our investment.

MR. KLIPPENSTEIN:  Then I'd like to change to conservation and demand-management programs.

If you turn to tab 7, we have a summary of THESL's CDM programs.  Do you see that?

MR. LABRICCIOSA:  Yes.

MR. KLIPPENSTEIN:  And I see three sections and three grand totals under the column of "total costs", one for 8.357 million, 8.542 million, and 5.199 million.  Do you see those?

MR. LABRICCIOSA:  Yes.

MR. KLIPPENSTEIN:  Now, I'm going to do a grand total of those grand totals, and I get 22,098,000, so approximately 22 million, for a total conservation budget.  Is that accurate, subject to check?

MR. LABRICCIOSA:  Well, subject to check. I'm trusting your math; I would say it's correct.

MR. KLIPPENSTEIN:  As we noted before, Toronto Hydro's total three-year budget for supply-side infrastructure is 906 million, approximately 900 million.  And if I do that simple math, it seems to me that for every dollar you are spending or proposing to spend on conservation, you're proposing to spend $41 on supply, so a 41:1 ratio.

And in that context, if you could turn to Tab 8, which contains Hydro's response to Pollution Probe's Interrogatories 1 and 2, at the bottom of that table, I see that for the year 2006, Toronto Hydro's peak-day demand was 4,995 megawatts.  Do you see that?

MR. LABRICCIOSA:  Yes.

MR. KLIPPENSTEIN:  And if I turn the page to the Interrogatory No. 2 answer, the table at the bottom, in the line 2007, that peak became in that year, one year later, 4,686 megawatts, right?

MR. LABRICCIOSA:  Correct.

MR. KLIPPENSTEIN:  In other words, your peak-day demand dropped in 2006/2007, right?

MR. LABRICCIOSA:  The numbers show that, yes.

MR. KLIPPENSTEIN:  If I do that calculation, I get a drop of 6.2 percent.  And despite that drop of 6.2 percent, I also see the numbers going up again in that table on Interrogatory No. 2 answer, that for 2008, 2009, and 2010, compared to 2007, the peaks are going up again, right?

MR. LABRICCIOSA:  That's correct.

MR. KLIPPENSTEIN:  And I don't see any load forecast or conservation forecast for time periods beyond 2010; is that right?

MR. LABRICCIOSA:  I don't think we've supplied them.  I think if you're referencing the previous table, those are OPA-funded programs, and they only go until 2010.

MR. KLIPPENSTEIN:  Well, I'm just looking at the sentence above the table that says:

"THESL has not produced load forecasts beyond 2010."

MR. LABRICCIOSA:  Right.

MR. KLIPPENSTEIN:  Okay.  Well, we asked in that context some questions about studies for more aggressive CDM programs.  If you turn to Tab 9, we asked for what studies Toronto Hydro has done with respect to the potential for more aggressive CDM programs to, (a), first of all, increase system reliability.  And your answer below is none, basically.

We asked for studies you might have done about potential for more aggressive CDM to reduce the ten-year capital budget, and you haven't undertaken any such things.  Same thing for reducing customers' electricity bills or any combination thereof.

So we have a very large supply budget of 900 million, compared to a tiny fraction of that for CDM, and we do see a drop from 2006 to 2007, which is great, but then you're upping it again for future.  But we don't see any studies about the possible CDM response to that.  Are you planning any such studies?

MR. LABRICCIOSA:  There are no studies directed at the specific questions you've asked around increasing reliability, altering the magnitude of the capital budget or reducing customer electricity bills, but most of our work has been at achieving conservation targets.  I think if you look back, our historical spend is over $60-million to achieve the results we have to date.

I would suspect one would say that our learnings part of the study is what we're trying to understand in how conservation works and what incents customers.  If you're asking specifically in those three areas of reliability, capital investment, or reducing electricity bills, we have no intentions to study those as part of this plan.

I would also draw your attention to -- you keep coming back to the comment of 900 million on the supply of the system.  The 900 million is really to address replacement of failing infrastructure, and that's really the delivery aspects of the system.  It's not aimed at bringing in new supply, but rather repairing a failing asset, replacing it.

MR. KLIPPENSTEIN:  However, in replacing it, you haven't done any of these studies to see if you could specifically replace it in a way that enhances the conservation?

MR. LABRICCIOSA:  Again, I think the evidence is in front of you.  There's $22-million in future earmarked at conservation, which is embedded in this plan.

MR. KLIPPENSTEIN:  Right.

MR. LABRICCIOSA:  We talked about the losses and the go-forward view of buying lower-loss equipment and designing the system for lower losses, but the thrust of this plan in front of you is really aimed at the reliability of the grid in replacing equipment that is failing.

MR. KLIPPENSTEIN:  All right.  I'd like to turn to issue 7.3, which is the fixed monthly charges.

MR. LABRICCIOSA:  What tab?

MR. RODGER:  Mr. Klippenstein, that would be another panel.

MR. KLIPPENSTEIN:  That's another panel, but can I give it a try here?

MR. RODGER:  No.  We'd like to move that to another panel.

MR. KLIPPENSTEIN:  I think, Mr. Chair, those are all my questions.

MR. SOMMERVILLE:  Thank you, Mr. Klippenstein.

MR. KLIPPENSTEIN:  Thank you very much, Members of the

Panel.

MR. SOMMERVILLE:  Mr. DeVellis.

MR. DeVELLIS:  Thank you, Mr. Chairman.

MR. SOMMERVILLE:  Mr. DeVellis, it's a quarter to 11.

Normally we would take our morning break around 11.  Does your schedule of questions sort of fit with that model?

MR. DeVELLIS:  Well, I have about 45 minutes, so I can stop at 11 or --

MR. SOMMERVILLE:  All right.  Why don't we do that?

MR. DeVELLIS:  Okay.

MR. SOMMERVILLE:  Thank you.

CROSS-EXAMINATION BY MR. DeVELLIS:

MR. DeVELLIS:  Good morning, panel.

I want to ask first about the process in establishing the capital plan that you've presented before the Board.  I know that some of those questions have already been addressed by panel 1, but I just have a few questions in that area.

In the 2006 decision from the 2006 rates case, the Board had, I guess, directed you to provide a capital plan.  And that was released in April 2006; is that right?  Or you could take it subject to check.

MR. LABRICCIOSA:  Subject to check.

MR. DeVELLIS:  And I think we heard earlier that by about August of '06, you had had a capital plan ready that's pretty much the same as the one that you presented here; is that accurate?

MR. LABRICCIOSA:  That's correct.

MR. DeVELLIS:  I just want to understand the relationship or the role that the Kinectrics asset condition study played in your capital plan.  I see that that study, which is in your evidence, is dated

February 2, 2007?

MR. LABRICCIOSA:  That's correct.

MR. DeVELLIS:  Okay.  Can you help me understand how that study played into your plan, if it was pretty much a done deal by August of 2006?

MR. LABRICCIOSA:  Well, I'm glad I said subject to check.  I think what we filed in front of you with the ten-year capital plan is dated January 2007.

MR. DeVELLIS:  No, I understand that, but we've heard evidence in the earlier panel that by August of 2006 you had in your business plan capital spending projections which are fairly similar to what you have in the capital plan here.  I understood from Mr. Haines that the plan was really set at that time.  There were some iterations of it after that, but basically it was done as of August of '06.

MR. LABRICCIOSA:  Right.  If your question's aimed at how did the two pieces of evidence form together, we used the asset condition assessment as a check to corroborate the capital plan; so in other words, the capital plan is predominantly based on age and performance, and factors those two elements in.

We used the condition assessment to corroborate the conclusions in that plan, and then factored in changes from there.

MR. DeVELLIS:  All right, so it was sort of an after-the-fact --

MR. LABRICCIOSA:  It was a supporting document; correct.

MR. DeVELLIS:  Thank you.  And can I ask you to turn to Interrogatory Response to the School Energy Coalition No. 42, and that's Exhibit R1, Tab 5, Schedule 42?

I apologize for not being as organized as

Mr. Klippenstein.

MR. LABRICCIOSA:  We have it in front of us.

MR. DeVELLIS:  Okay.  And what we did there is we took columns in your capital plan and amalgamated them into one table.  And you'll see that we have the first column is -- let me back up.

In your capital plan, you mention that you have these two methods of evaluating the condition of your system.  One is an age-based assessment and one is a condition-based assessment.  And the two methods, you say, produce similar results for certain assets and dissimilar results for others, and you list the categories in the capital plan.

What we've done is we took the two: the number of units to be replaced according to both methods -- which is in the plan -- and then we added another column, which was the recommended unit replacement, the number of units that you've recommended to be replaced in your capital plan.

Have we done that accurately there?

MR. LABRICCIOSA:  Yes, I think so.

MR. DeVELLIS:  Okay.  And I think you also say somewhere in your capital plan that the number of units to be replaced forms the basis for your capital spending requirements; is that fair?

MR. LABRICCIOSA:  That's fair.

MR. DeVELLIS:  Okay.  Can you help me understand how you arrived at the number of units to be replaced, because if you compare the two columns, the first column and the second column and then the third column, the numbers don't always match, and sometimes you have a recommended number of units that's lower than both estimates, sometimes higher.  Sometimes it's between the two, which I guess we could understand, but it's the ones that are higher or lower than both estimates that I don't understand.

MR. LABRICCIOSA:  Sure.  And I think you asked that in the interrogatory.  And the response was that for the ones that -- you've talked about a couple of asset classes where the replacement units are lower than suggested by either age or condition.

MR. DeVELLIS:  Right.

MR. LABRICCIOSA:  And there were two reasons for that.  The first one of which is, when you look at transmitters, for example, if you're going to convert or decommission a transmitter, you wouldn't necessarily replace it because you're eliminating those types of assets from the system.

So, for example, if you convert 4 kV to 27, you eliminate a station, you likely eliminate hardware out on the street, which exists for 27, but you eliminated it for 4 kV, so you would need fewer poles, fewer of those types of transformers.

The other reason for that was also the element that we could maintain equipment rather than replace it, to keep it in a fair condition, and eventually deal with the replacement further out.

So, while the condition factors in what the state of the component is today, our view is we can maintain it, going forward, to push out the replacement.

MR. DeVELLIS:  Okay.

MR. LABRICCIOSA:  So that's why it would be lower in our plan, relative to what both the age or the condition was saying.

MR. DeVELLIS:  Okay.  I'm not sure I'm quite following you, but maybe we can use specific examples, and you can explain.

Station transformers; the first row?

MR. LABRICCIOSA:  Mm-hmm.

MR. DeVELLIS:  147, 142, and your recommended unit replacement is 61.

MR. LABRICCIOSA:  Correct.

MR. DeVELLIS:  Can you explain that?

MR. LABRICCIOSA:  So as an example, the voltage conversion, if a station transformer is eventually not needed, we wouldn't replace it.  So when we convert the load supplied by that station to another voltage level, we would eliminate that station.  So therefore, we wouldn't put the capital investment in place to replace it.

MR. DeVELLIS:  Okay.

MR. LABRICCIOSA:  So that's an example of one; we wouldn't replace that asset.  We'd keep it in, stretch it out for a little longer until we convert the load, and then eliminate the asset entirely.

MR. DeVELLIS:  Okay.  Submersible transformers; 2,209, 2,101, and then 6,118.

--- Reporter appeals.

MR. DeVELLIS:  6,118 is your recommended number.

MR. LABRICCIOSA:  So that would be the part C of your interrogatory, which sort of hinted at why in some cases assets that are being replaced or recommended to be replaced are higher --

MR. DeVELLIS:  Right.

MR. LABRICCIOSA:  -- than what's found in both of the studies.

MR. DeVELLIS:  Yes, I know you've answered that.  I just didn't understand the answer.

MR. LABRICCIOSA:  Sure.  So in a case with the underground cable, for example, there's a connected -- they're connected assets.  So a cable is connected to a transformer, which is connected to a service to a home.  If the --

--- Reporter appeals.

MR. LABRICCIOSA:  Oh, I'm sorry.  To a home.  I should probably speak into this mic.

So in that particular case, if you're going to replace the cable and put the effort in to replace it, keeping in mind that the existing infrastructure's on one side of the street, energized and connected and supplying the home, we have to rebuild the infrastructure on the other side, and therefore require a transformer, as well as service connections, as well as civil infrastructure.

So while we're trying to deal with a failing asset on cable, especially in direct buried cable, our method of replacement will inherently include the transformers, the civil infrastructure, and the service connections to the home.

So in that particular case, we're forced to replace the cable, or our plan is to really address the cable.  Inherent by design is the connection of transformers and other services as part of that, so that's why we have more in submersible types.

MR. DeVELLIS:  Okay.  Is it fair to say then you're sort of accelerating your replacement of other certain assets, because you're already in there replacing something that you really need to replace?

MR. LABRICCIOSA:  Yes.

MR. DeVELLIS:  Okay.  You mentioned cable.  You have underground cable XLPE in ducts.  No number of units for the condition-based assessment.  And you have 401 kilometres, I guess?  Is that -- Sorry, for the condition-based, you have 401 kilometres; nothing for the age-based.  Is that because they haven't reached end of life, according to your age-based analysis?

MR. LABRICCIOSA:  No, the age-based analysis, I think the caveat in there, in the plan, describes it as lack of information, so as part of the amalgamation, we all came together at a point in time in 1998 through 2000.  We're still merging systems, collecting data, trying to consolidate databases.

I think you heard earlier we've just finished -- you heard a term called GEAR, or geo-spatial system.  We've just finished putting that platform together, in terms of a consolidated platform which houses some of this data.

So at the time we did some of this study, we didn't have age information, and I think the ACA also pointed out that, you know, there are some gaps in data that have to be closed, and so we are putting those data collection initiatives or efforts together as we speak, going forward.

MR. DeVELLIS:  Okay.  And earlier, when we were talking about the process of coming up with the capital plan, and you said that the condition-based assessment was an after-the-fact aid -- but I take it then when you did capital plan initially, if you didn't have any age-based information, did that mean that you didn't have anything in there for underground cable replacement?

MR. LABRICCIOSA:  I'm sorry, can you repeat the question again?

MR. DeVELLIS:  Well, earlier we were talking about the process of how you came up with your capital plan you presented to this Board, and you said that, well, it was basically done in August of 2006, but supplemented by the Kinectrics study, the condition-based assessment.

But that would suggest to me that if you didn't have age-based information for underground cables, that you couldn't have any forecasted expenditures in your original capital plan for underground cables, because you didn't have age-based information.

MR. LABRICCIOSA:  No, we have performance data as well that shows that cables do fail, and again, it's deteriorating performance in that area of the system that caused us to look at things like the ten-year plan and the asset condition assessment.  We also included as part of our submissions the cable study plan.

So based on our performance, was focusing us in that particular area, causing us to collect better data to make better plans and decisions.

And again, the majority of that effort really focused in on the investment in this first phase, on the underground components.

MR. DeVELLIS:  According to the condition-based replacement people, the recommendation was to replace 401 kilometres of underground cable XLPE, and you're recommending 561 kilometres.  You may have already explained that, but if you did, I didn't catch it.

MR. LABRICCIOSA:  Again, I would turn you to a cable study that was completed by John Densley, which is really -- it's listed as Exhibit R1, Tab 3, Schedule 25, Appendix "B".  I've just noted for the reference that it's a very detailed study that explains the condition of the cable, even though, at a cursory level, when Kinectrics did their review, there really wasn't a lot of corroborating evidence on condition that can be collected to identify that the system is probably in a condition worse than what the data is showing today.

For example, in Densley's report it talked about using probes and dielectric receivers, acoustic emission receivers, to identify which cables are failing, because that would give better indication of the quality or the condition of the asset.

From his information, we're extrapolating that the system is worse, and as well as, from the performance data, it is performing worse than what it's telling us, hence leading us to the conclusion we would have to get at it a lot sooner.

MR. DeVELLIS:  Thank you.

Mr. Chairman, I'm about to move on to another area.  Would this be a convenient time to break?

MR. SOMMERVILLE:  Thank you.  We'll take a break.  We'll resume at 11:15.  Thank you.

Oh, just for everyone's information, the Board has a commitment over the lunch break, so we'll take lunch from 11:50 to 1:30.  Thank you.

--- Recess taken at 11:00 a.m.

--- On resuming at 11:20 a.m.

MR. SOMMERVILLE:  Please be seated.  Thank you.

Mr. DeVellis.

MR. DeVELLIS:  Thank you.  Can I get you to turn to

Interrogatory Response No. 27 to School Energy Coalition?  It's Exhibit R1, Tab 5, Schedule 27.

We asked you for your unit costs for your underground direct buried cable replacement, and I just want some clarification here, because when we add up your per-unit cost and multiply by the number of units, we get approximately $256,000, and it just struck me that that can't be correct.  I think your budget is actually $45-million.

MR. COUILLARD:  I'm not sure which unit.  Are you doing all three tables in terms of units?

MR. DeVELLIS:  Yes.

MR. LABRICCIOSA:  And are you using conductor lengths and cables or circuit lengths?

MR. DeVELLIS:  You lost me there, but you have the number of units up on top, number of kilometres?

MR. LABRICCIOSA:  Right.

MR. DeVELLIS:  So, 180, 124, 130, and we took a total unit cost for the three phases, I guess, and added them up.

MR. LABRICCIOSA:  I don't think you can just add them up like that.  Sorry, I haven't really looked at your calculation.

MR. DeVELLIS:  All right.  We have other interrogatories where we've asked for that and we've taken your total unit costs and multiplied by the units, and it came out to whatever your budget was.  And this one we couldn't do that.

MR. LABRICCIOSA:  Again, I'm sorry, I can't speak to how you did your calculation.  If you're asking us to explain the difference between your calc. and what the table presents here, I don't think we can do that there.

MR. DeVELLIS:  Well, I tell you what, we added $534 for example, for 2008, so unit costs 534, plus 245, plus 345, multiplied by 230.  So it comes out to a total unit cost of $1,114 multiplied by 230.

MR. LABRICCIOSA:  And, again, those are three different types.  What you're seeing is a breakout by three different types of cable replacements, so they're not on equal ratios.

MR. DeVELLIS:  So you can't add them.

MR. LABRICCIOSA:  I don't think you can.

MR. DeVELLIS:  All right.  That's fine.

Can I ask you to turn to Schedule 33 of the same exhibit?

MR. LABRICCIOSA:  Okay.

MR. DeVELLIS:  Again, we asked for your unit costs for your transformer station replacements, and if you could turn to table 4, which is on page 4.

MR. LABRICCIOSA:  Yes.

MR. DeVELLIS:  And you say in the explanation that's at page 5 that the cost variance shown in table 4 from

2007-2008 is attributed to the fact that for 2008 and beyond, the circuit breakers to be replaced are outdoor bulk oil circuit breakers, which are more expensive to purchase and install than indoor metal-clad circuit breakers, which were replaced in 2007.

MR. LABRICCIOSA:  That's correct.

MR. DeVELLIS:  Now, if you look at the material costs that are in table 4, the per-unit cost -- those material costs, that's the total?

MR. LABRICCIOSA:  Yes.

MR. DeVELLIS:  And so to get per-unit, you divide by the number of units.

MR. LABRICCIOSA:  Sure.

MR. DeVELLIS:  So the math is there.

MR. LABRICCIOSA:  It's good for that one, yes.

MR. DeVELLIS:  And we actually have the per-unit cost decreasing from $23,000 to $17,000 for material, which is not what we're concerned about.  It's the next line, the labour costs, the per-unit costs.  Well, you can just see from the numbers that the per-unit cost for labour, the total is the same, but the number of units are much lower in 2006 -- the per-unit costs are much higher for labour.  Can you explain that?

MR. LABRICCIOSA:  Yes.  It's different equipment when you're going from 51 to 4.  You've obviously seen that.

MR. DeVELLIS:  Yes.

MR. LABRICCIOSA:  And the explanation really deals with the 51 are encapsulated units, self-contained, sort of pre-packaged, slide them in.  That's why the amount of labour and effort to replace those is a lot less; hence the cost per unit being lower.

The outdoor type, you're dealing with a higher voltage.  Outdoor requires more effort, not only effort to install but a lot of effort working around the energized equipment outside, so it takes longer to replace.

MR. DeVELLIS:  I'm just a little confused why the unit itself actually costs less, but it takes a lot longer to install it.

MR. LABRICCIOSA:  Again, because the four units that you see from 2008-2010 are 27,000-volt units.  The numbers in the 2007, the bridge year, the 51 units are for 4,000-volt units so, again, it's just that they're not necessarily compatible or comparable in terms of type of effort to install.  Safety procedures around higher voltages versus lower voltages.  As well as the 51 units are pre-packaged and sort of slide-in type installation, whereas the other units, you have to break them down, get them back in, and build them back up.

MR. DeVELLIS:  Okay.  I have a question next about your reactive capital spending.

You say in the evidence -- you don't have to turn it up, but you can if you want.  It's at D1, Tab 8, Schedule

2.  The evidence is, the reactive capital requirements increase substantially in the bridge year to address a significant increase in system failures, resulting from the growing base of aging assets.

And then at our Interrogatory No. 35, we asked you for a breakdown of the number of work requests by type of equipment.  Maybe you could turn to that.

MR. WONG:  Yes.

MR. DeVELLIS:  And we added up the totals of your various tables there, and again, perhaps my math is wrong again, but what we did is just added up the totals on each table.  And we have here number of work requests actually decreasing from 2006, 7,454, to 5,755 in 2007, and then staying at about that level, going forward.

MR. WONG:  That's true, but the mix of the units are

different.  What you see on table 4 is that the underground units are increasing, and those costs are generally higher than for the other types of units.

MR. DeVELLIS:  Sorry, total underground units are increases?

MR. WONG:  Correct.

MR. DeVELLIS:  You're looking at table 4?

MR. WONG:  Yes.

MR. DeVELLIS:  That's actually decreasing.

MR. WONG:  Oh, from '06 to '07.

MR. DeVELLIS:  It's decreasing, yes.

MR. WONG:  Yes.  In the test years they're -- are you referring just to from '06?

MR. DeVELLIS:  Well, from the evidence in the bridge year, the number of work requests is increasing.  This is showing that from 2006 to 2007 the work requests are decreasing.

MR. WONG:  Sorry, can you repeat the question?

MR. DeVELLIS:  You had pointed to the underground efficiencies, I guess, as the reason for the increased expenditures in this area, but it looks like those are decreasing, if you look at table 4.

MR. WONG:  Yes, but again, it's also the mix of those units as well.  There are lower-costs underground units versus higher-costs underground units.  And I think what you're seeing -- what it shows is that the lower-costs underground units are decreasing, whereas the higher-costs ones are increasing.

MR. DeVELLIS:  I don't want to dwell on this for too long, but are there some in here that jump out at you that are the higher-cost ones?

MR. WONG:  Well, for instance, the underground secondary service repairs are -- we're seeing lower volumes of that.  So that would be a factor for the decreasing units going forward.

If you'd like a better explanation, I would have to defer.

MR. DeVELLIS:  I don't think it's necessary.  I thought there would be a quick answer, though.

I'll move on to my last area of questions, and it has to do with your response to our Interrogatory No. 44, which is R1, Tab 5, Schedule 44.

MR. WONG:  We have that up.

MR. DeVELLIS:  I'm looking at Part C, and we asked for an explanation of the variation in the sustaining capital spending from the distribution capital plan, and in your evidence, your prefiled evidence in this proceeding, the answer you gave was that the capital plan used 2007 dollars, whereas the evidence -- the figures in your prefiled evidence -- represent actual projections for 2007 and forecasted amounts for 2008, '09, and '10, taking inflation effects for the various project components into consideration.

MR. LABRICCIOSA:  Correct.

MR. DeVELLIS:  So does that mean that the capital plan, the amounts that we see in there, the only variation we would see would be due to the changes in work?

MR. LABRICCIOSA:  Correct, volume of work.

MR. DeVELLIS:  So they're all fixed at 2007 --

MR. LABRICCIOSA:  Dollars.

MR. DeVELLIS:  -- dollars.

MR. LABRICCIOSA:  It doesn't assume inflationary effects for materials and labour and those kinds of elements.

MR. DeVELLIS:  Those are all fixed.

MR. LABRICCIOSA:  When we put this plan together, the EDR, presuming we put our budgets together, we used the wage rates in those respective years, given the assumptions we gave in the assumptions section of the filing.

MR. DeVELLIS:  And materials costs and wages and all of that --

MR. LABRICCIOSA:  Right.

MR. DeVELLIS:  -- would be fixed in the capital plan, but not in the prefiled evidence?

MR. LABRICCIOSA:  Correct.

MR. DeVELLIS:  Okay.  Thank you very much, panel.  Those are my questions.

MR. SOMMERVILLE:  Thank you, Mr. DeVellis.

Mr. Faye?

CROSS-EXAMINATION BY MR. FAYE:

MR. FAYE:  Thank you, Mr. Chair and Panel.

I'd like to start just by reviewing a couple of items that I found a little confusing in the cross by other of the intervenors.  And starting with Pollution Probe's examination of distributed generation, it seemed to me that one of the reasons why distributed generation would be limited on THESL's system is this issue of short-circuit availability.  And I wonder if you could just describe in layman's terms what short-circuit availability means, so that the Panel understands that.

MR. LABRICCIOSA:  Short-circuit availability or capacity deals with the ability of the system and the design to protect itself against cascading failures.  In other words, as you connect more resources to that grid, you have to have the means to interrupt failures, should a failure exist.

For example, if you were to connect more resource capability to that section of the grid, and you exceed the short-circuit capability, the ability of the system to protect itself against any one failure is compromised.

So in other words, it can take down the entire grid, it could cascade out, prevent, you know, huge -- more than designed damage during a failure condition.

Is that a fair enough explanation, Mr. Faye?

MR. FAYE:  Yes, I think that's very understandable.

And the contribution that distributed generation makes to that issue is that, if you have a generator on a feeder, it's available to feed current into a fault if a fault occurs, and you could exceed the limits of your system in so doing; is that correct?

MR. LABRICCIOSA:  That's correct.  DG is considered a source of current, or energy, into that failure.

MR. FAYE:  Now, are there measures that didn't get discussed that you can employ on your system to limit the amount of short-circuit availability at any given point in the system?

MR. LABRICCIOSA:  There are.  You can buy -- again, it's by design.  You can buy higher-rated components.  I'm not sure how much detail you want me to get into, but essentially you can mitigate limits by design of systems or buying additional components.

MR. FAYE:  Okay.  And I think where I'm going with this is just to clarify that the response seemed to say that there's limits on the system introduced by short-circuit considerations, and I'd just like the Panel to be aware that you're saying there are some technical solutions possible to that, which you haven't necessarily implemented, but if the circumstances were right and a distributed generation project came along that needed some technical assistance on short-circuit, there are solutions available?

MR. LABRICCIOSA:  It would have to be looked at on a case-by-case basis.  And again, there are, you know, technical solutions available depending on the situation of the problem at hand.

MR. FAYE:  All right.  Another point that Pollution Probe was asking you about, and I think I was left with the wrong impression.  I just want to clarify so the Panel hasn't been left with the wrong impression, and that is this issue of distribution line losses and the relationship between that and current.

I think the discussion sort of left the impression that losses are directly related to the square of the current, and that that's the reason why the rate of loss, the percent rate of loss, should increase as you put more load on a feeder.

I just wanted to clarify with you, is it the fact that you're putting more load on the feeder, or is it the fact that the impedance of the circuit, the alternating current equivalent of resistance, is a non-linear function?

MR. LABRICCIOSA:  You're correct.  It's the fact that the impedance is a non-linear function.  I was a little confused by his line of questioning, in a sense that there are many factors that go into losses, both technical and non-technical.

And I believe his line of questioning, the way he was presenting his question, was really trying to arrive at a conclusion that, as the day peaks, there are more losses.  And it's really a percentage, and the percentage is linear over that period.

But, you know, there are -- in a non-technical loss area, there are behaviour issues around how you deal with theft of power or diversion of power, as well as models that deal with flat-rate billing.

So those present the non-linearities that I was trying to arrive at.

MR. FAYE:  No, but --

MR. LABRICCIOSA:  But as a whole, the non-linear aspects of impedance is what drives the non-linear elements.

MR. FAYE:  So what we'd like to leave on the record clearly is, if you ignore the sources of losses that aren't directly attributable to the current running through the line, such as people stealing power, if we just consider the current on the line, the percent loss does increase at a non-linear rate as you put more current through the wire, but it's because the wire heats up, and as the wire heats up, the resistance increases.

MR. LABRICCIOSA:  Correct.

MR. FAYE:  So Pollution Probe's conclusion that there is a non-linear function attributed to percent is true; it's just they understood it for the wrong reasons?

MR. LABRICCIOSA:  Correct.

MR. FAYE:  Thank you.

I'd like to return to an issue that came up before the prior panel that my co-counsel, Ms. Campbell, asked yesterday, and the previous panel said that that would be a more appropriate question for this panel to answer.

I think she was attempting to discover how much of the increase in manpower that you forecasted over the test year is attributable to this capital program expansion.  And she was going to refer you to an exhibit, which is a graph, and it's Exhibit R1, Tab 6, Schedule 5, Appendix "A".  I'm not sure that she was directly interested in the actual numbers on this, but was more interested in following the trend line here and getting an answer to that question as to how much is being driven by capital investment here.

MR. LABRICCIOSA:  That question came up several times,

I think, during the hearing.  And I think my sense is, people want to de-couple or break out the elements of staff addition into individual components.

In actual fact, the staffing plan you see there is in preparation -- predominantly driven by the aging workforce that are going to be leaving the organization.

Notionally, with the increase in capital spend and the forecast in diminishing resources or the resources retiring from the organization, in general, we know we're going to have to add.  We have more work.  We have fewer people expected.  We're going to have to add people to make up the difference.

On top of that, what amplifies that is it takes four years to actually replace leaving talent with incoming talent, and one would argue that, even after the four years, the amount of knowledge that's retained when a

35-year veteran leaves versus someone who's just come in at five years, I don't think you can equate that.  So there's still also a bit of latency or lag period when that new employee comes up to speed and can be a fully productive employee replacing one that has left with the level of experience he or she left with.

The root of the question always comes back to, well, how many are related to this particular component, which is just increased capital.  We don't have that absence.  What we've presented in front of you encapsulates the components I just described to you.  An increasing capital spend, an expectation that the workforce is declining, based on age and retirement forecasts, coupled with the fact it takes four years to ramp up this new resource to contribute to the organization at a level that the person who has left.

MR. FAYE:  Do I understand you to say, then, that ignoring the apprentices who apparently are not going to be a hundred percent productive for some time, would you agree that, with the ramp-up of your capital, you have insufficient staff right now to cope with that?

MR. LABRICCIOSA:  No, I wouldn't necessarily agree with that statement, Mr. Faye.  I think I would say that we have the resources today to undertake the plans we put forward, if staff were not retiring in the future that we see coming forward with the aging workforce.

It is the fact that they are retiring means we have to start now to prepare for that replacement in order to keep our effort in work production at the levels today.

MR. FAYE:  If you were able to take these retirements out of the equation and you could count on all the staff that you have right now being available, do I understand you say that you would be able to cope with your work program without having to add all these apprentices?

MR. LABRICCIOSA:  That's correct.

MR. FAYE:  Would you agree that your work program has expanded between the historical year and the bridge year and test years?

MR. LABRICCIOSA:  Correct.

MR. FAYE:  Well, am I to conclude, then, that your staff wasn't a hundred percent occupied in the historical year?  If they were all fully occupied in the historical year, and you're adding work, how could they do the new work?

MR. LABRICCIOSA:  No, I wouldn't necessarily say they weren't fully occupied.  I think we'd say we would explore new techniques and methodologies to make our staff more productive and implement new processes and look for efficiencies along the way.  And we have an expectation that we will capture that efficiency going forward, to make up the difference in this plan.

MR. FAYE:  If we look at this nice exhibit here, D1,

Tab 7, Schedule 1, and this one, if you could take it out and just keep it handy, because I'm going to refer to this quite a lot throughout the cross-examination.

It's page 10 of that schedule, and it's a chart called "Summary of capital budget."

Looking at "Total distribution system," this is probably the line that's most indicative of how much manpower you need in your line construction and line maintenance department; would that be so?

MR. LABRICCIOSA:  Embedded in those sustaining capital budgets or the total distribution system is also work we do with external contract resources like civil construction.  I think you mentioned that earlier.

So if you include that in your statement in terms of all resources, I would say yes.

MR. FAYE:  Okay.  Well, looking at the historical year, the number is 124 million; is that right?

MR. LABRICCIOSA:  That's correct.

MR. FAYE:  Then going to the bridge year, we jump to

167 million.  And just in rough terms, that looks like about a 30 percent increase; would you agree there?

MR. LABRICCIOSA:  Yes.

MR. FAYE:  Then going up to the 2008 test year, it looks like an increase of probably close to 90 percent, maybe 85 percent?

MR. LABRICCIOSA:  Yes.

MR. FAYE:  And it only increases from there.  The 2009 test year is even higher; 2010, higher yet, although the rate of increase does drop off.  If I understood you correctly, are you suggesting that you're going to get almost a hundred per cent productivity improvement between now and 2010?

MR. LABRICCIOSA:  No, sir.  I wouldn't conclude that.

I would say there are many factors that contribute to that increase.

An example that we just talked about was use of civil construction resources.  When most of our effort is at rebuilding our underground system, there's a greater cost associated with rebuilding that system, involving a civil component.

We do not do that internally in the organization; we contract that out, so that element increases.

MR. FAYE:  How much would you attribute to the civil component?

MR. LABRICCIOSA:  There is an exhibit that deals with contracts, and I think it would be in there.  It's roughly double, I would say.  I would say it went from -- subject to check -- 20 to 40 million, but I could look that up.

MR. FAYE:  So, of the 2008 test figure there, what's the best number to compare to, the 228 total distribution system, or the 115 total sustaining capital?  Which is most applicable?

MR. LABRICCIOSA:  I'm sorry, what's the question again?

MR. FAYE:  When we're talking about civil construction expenditures that are contracted, and what I want to do is -- you said it's gone to 40 million.  Do I compare that 40 million to the 228 total, or do I compare it to the 115?  Is all that 40 in the sustaining capital section, I guess is the question.

MR. LABRICCIOSA:  Not all of it; a predominant amount of it.  There are some elements in reactive and customer connections work which is below that line.

MR. FAYE:  All right.  Well, then let's stay at the total distribution system line.

MR. LABRICCIOSA:  Sure.

MR. FAYE:  In the 2007 bridge year, the 167, do I understand you to be saying that about 20 million is civil contracts there?

MR. LABRICCIOSA:  Correct.

MR. FAYE:  And of the 228, about 40 million is civil contracts?

MR. LABRICCIOSA:  Correct.  Again, subject to check on that contract statement.  I'm just trying to recall the exhibit.

MR. SOMMERVILLE:  Mr. Faye, we have a hard-edged obligation that we have to meet, so we're going to --

MR. FAYE:  We can leave this here, because the panel looks like they need a little time to look this number up.

MR. SOMMERVILLE:  We're going to break at this stage, and we will resume at 1:30.  Thank you very much.

--- Luncheon recess taken at 11:51 a.m.

--- On resuming at 1:31 p.m.

MR. SOMMERVILLE:  Thank you.  Please be seated.

Any preliminary matters, Mr. Rodger?

PREMILINARY MATTERS:

MR. RODGER:  Just one, Mr. Chairman.  I've handed up to Mr. Faye, and will give to you an update, and this was discussed yesterday during this panel.  I believe, Mr. Warren, it's an update to Exhibit R1, Tab 1, Schedule 4-1, Appendix "B".  And these were the changes to the return on equity.  It's an update of the page of Appendix "B", THESL financial data, years ended December 31st.

In speaking to a couple of my friends here,

Mr. Chairman, I thought it might be helpful if I just asked at this time Mr. Jamal to explain this update.  Particularly, there were some questions my friends have raised in terms of the difference between what actual return on equity is, and what allowed return on equity is, and why in particular the actual return on equity is lower than the allowed return on equity for 2008.

With the Board's permission, I wonder if perhaps

Mr. Jamal might be able to explain that.

MR. SOMMERVILLE:  I think that would be helpful.  Thank you.

MR. JAMAL:  Thank you.  Mr. Warren had asked some questions yesterday around return on equity.  I had indicated that in the pro-forma financial statements there was an administrative error related to that, that needed to be updated.

The impact of those changes to the pro-forma financial statements which were issued yesterday have been reflected in two of the interrogatories that were handed out earlier this afternoon, just a moment ago.

The actual return on equity for 2007, '08, '09, and '10, are now 9.3 percent, 6.7 percent, 9.3 percent, and 10.2 percent, respectively.

The actual or projected return on equity is based on an accounting formula which is essentially net income divided by the average equity.  The allowed return on equity is based on a prescribed formula, which is described

in Exhibit P.  So, although they have the same name, they're derived using two totally different methods, so they're not directly comparable.

MR. RODGER:  What's the significance of the difference between these two concepts?  What should the Board take from these different numbers over the different years, depending on whether it's actual return on equity or allowed return on equity?

MR. JAMAL:  The actual projected return on equity has different factors, or different factors affect that.  For example, dividends and any other changes in equity.  Those factors don't affect the prescribed or allowed return on equity, because that's based on a formula.

MR. RODGER:  Maybe just one final question, and this comes from my friend from Schools, who I don't believe is any longer in the room, but he would like to understand why in 2008 the actual return on equity is lower, 6.7 percent, as opposed to the allowed return on equity which is now shown as 8.8 percent.  Why is the actual return on equity lower?

MR. JAMAL:  I believe a lot of that had to do with the operating costs differential, and any changes in net revenues or operating expenses that affect revenue will impact this.  And at a high level, I believe that it was higher costs and the net revenues that impact this.

The specific differences are described in Exhibits F1 and F2, which will clarify why that's the difference.

But, once again, there are two different formulas, and they are driven by different aspects.

MR. RODGER:  Thank you, Mr. Chairman.

MR. SOMMERVILLE:  Thank you.  It occurs to me,

Mr. Rodger, although not all of the intervenors are present, and Mr. DeVellis in particular, that it may be worthwhile, if there are some questions arising from your questions, then it may be worthwhile to here if Mr. Buonaguro, for example, has questions or questions from the Board.

Mr. Buonaguro, do you have questions?

CROSS-EXAMINATION BY MR. BUONAGURO:

MR. BUONAGURO:  Just following up to make sure I understand it, I took it from what you are saying that when you make your application I'm assuming that you make your application with the intent, from a regulatory perspective, of meeting the 8.8 percent allowed return; right?

MR. JAMAL:  Yes.

MR. BUONAGURO:  And that the 6.7 actual is based on a projection of certain factors which aren't accounted for in a regulatory context?

MR. JAMAL:  Specifically, I'm not sure if it's specifically related to stuff that's not accountable.  But that's derived based on the projected net income, which, for the most -- and, sorry, there's also a dividends component in there that's not factored into the allowed return on equity.

However, primarily, that's going to be as a result of the variances caused, I believe, at a high level, subject to check, related to operating expenses.  I don't have the specifics in front of me right now, but this is purely a function of the $49.6-million worth of net income, as you can see in the line above, which is considerably lower.

MR. BUONAGURO:  Okay.  It's just because -- I think the questions arose because normally you don't forecast a shortfall between what you're supposed to -- and when you come forward over the test year, you calculate the test year at the allowed return on equity, and that's what –- you’ve structured your filing to meet that.

MR. JAMAL:  Yes.

MR. BUONAGURO:  And then, in the actual year, if you fall below it, it's because of bad weather or something; right?

MR. JAMAL:  Right.

MR. BUONAGURO:  On the gas side, at least.  And because you're forecasting a shortfall, it's a little confusing.

What I'm taking from what you're saying that that's because there are things that just aren't taken into account when doing the filing that happen every year.  So if other companies came forward and reproduced their actuals from previous years and their forward test years, if they were doing a multiple-year test year, in the same way, they would have the same sort of possibility of a shortfall, even though they wouldn't be planning for it?

MR. JAMAL:  Once again, I'm not exactly sure what's causing the shortfall based on the information I have available in front of me.

I would suggest that we probably look at this variance again, once all the proposed changes are factored in, after we've identified any of the changes that are required, and recalculate this number, and then do an assessment or an analysis.

MR. BUONAGURO:  I think that's as close as I'm going to come to understanding it.

MR. VLAHOS:  Mr. Jamal, I'll pick it up from here.

QUESTIONS BY THE BOARD:

MR. VLAHOS:  Frankly, I don't understand what this is all about.  This is a schedule based on financial data, and I see from the exhibit number, is this pursuant to a question or interrogatory by Staff?  I see an arrow "1" there.  Is that what this designates?

MR. JAMAL:  Yes.

MR. VLAHOS:  So why do you feel compelled to change this every time there is a change, unless you were asked specifically to make that adjustment by the person that perhaps has asked the question in the first place?

MR. JAMAL:  This change resulted from the update into the pro-forma financial statements that were handed out yesterday.  This was a downstream effect of that change.

MR. VLAHOS:  Okay, sir.  There are about 1,500 interrogatories, okay?  And I'm sure that a change in something would cause a change into more than just one schedule in the 1500 responses.  Why did you feel compelled to update this one?

Were you asked to?

MR. JAMAL:  Yes.  I believe Mr. Warren asked for this yesterday.

MR. VLAHOS:  He asked for it.  But I thought he asked for the update because you brought that to his attention; is that not the case?

MR. JAMAL:  I don't believe, sir, that was the case.

MR. VLAHOS:  How would that come up, then, Mr. Rodger?

MR. RODGER:  I believe it was part of Mr. Warren's cross-examination.

MR. VLAHOS:  Right.

MR. RODGER:  He wanted to confirm these numbers of both the actual and allowed return on equity, and that's when Mr. Jamal advised him that there was likely going to be a change, because of some of the other changes that have been talked about over this case.

MR. VLAHOS:  Okay.  Maybe I'm confusing this with the other blue sheets that --

MR. SOMMERVILLE:  If I may, I think there may be some miscommunication.  I think that, if I recall what happened, in going over the original response to the interrogatory,

Mr. Jamal, at that point, indicated for the first time that there were consequential changes to this exhibit as a result of the filings that had been made earlier yesterday morning, to the pro-forma financial statements.

What Mr. Warren asked for was the document that we now have, which was the correction that I don't think goes to your question, Mr. Vlahos, which is why in his testimony in cross-examination Mr. Jamal indicated that, "Oh, by the way, we have to change this as well."  I think that's right.

MR. VLAHOS:  Maybe I can just backtrack then and ask some specific questions about this schedule, and also another schedule, another update which I don't have in front of me, but it also, Mr. Rodger, was a blue update.  And that was a couple of days ago, and there was some questions, and I think Mr. Chairman has it in front of him, so I'm going to grab a copy in a few minutes.

Mr. Jamal, this is the financial data of the company that has actuals, it has bridge, and it has going forward.  Okay?

So if we look at the actual return or the allowed return, the second and third rows, what does it tell me?  It tells me in 2006 what was the actual return and what was allowed, and the company has earned more; right?  We know that without any qualifications.  That's a fact.

MR. JAMAL:  What you do know -- excuse me, was that a question?

MR. VLAHOS:  Yes.

MR. JAMAL:  What you do know is that the actual return on equity based on the accounting formula resulted in 11.3 percent.  The allowed return on equity, based on the prescribed formula, was 9.0 percent.  They're not the same formula.  They're just called the same thing.  That's --

MR. SOMMERVILLE:  Your point is that the actual return on equity as represented in this exhibit is not a like measure, so that I cannot compare the allowed return on equity to the actual return on equity, because they are fundamentally different formulae.

MR. JAMAL:  Yes, sir.

MR. VLAHOS:  Well, it must mean something, though.  I mean, if you compare one with another, it must mean something.  What it tells me is that the allowed return on equity -- that is, if the company were to earn precisely as they had forecast, or as what the rates reflected, it would have been 9-point percent, right?  Let's look at 2000, and it was a test year.

MR. JAMAL:  Yes.

MR. VLAHOS:  All right?  The company made an application.  It was a future test year.  The Board set the rates, okay?  And everything worked out just perfectly.  The two numbers will be the same.

MR. JAMAL:  I don't think that's the case.

MR. VLAHOS:  Okay.  So if it's not the case, then this is not a regulatory construct.  This is an accounting construct, and I'm trying to make some sense as to what use is this for me.

MR. JAMAL:  We provided the information that was requested in the interrogatory.  We, Toronto Hydro, didn't intend to make the comparison.  We just responded to the interrogatory as requested.

MR. VLAHOS:  All right.  So you responded to the interrogatory, and that's as far as it goes.  You don't put any significance as to how the numbers are for 2008, 2009, and 2010.

MR. JAMAL:  Correct.  We don't put any significance.

MR. VLAHOS:  All right.  Thank you very much.  That really clarifies it, because I can just put it at the bottom of my drawer now.  All right.  Thank you.  So I promise you I will not bother you with this again.

Now, it's not over yet, though.  Mr. Chair, may I have your indulgence, and just give me that?

--- Board confers.

MR. VLAHOS:  Yes, Mr. Rodger, one more time, if you don't mind, if you can be patient with me.

It's the purpose of -- and I'm looking at Exhibit B1, Tab 7, Schedule 1, Appendix "A" -- and those are the blue-sheet updates.  And again, since we're on the topic, if you don't mind, just remind me as to why they were updated -- I guess they're blue colour, so there must have been updates, and the reason for that, and what is the plan going forward.

So maybe you can help me one more time with it?  And if you would rather leave that in my discussion with the regulatory people later on, that would be fine as well.

--- Pause in proceedings.

MR. RODGER:  Sir, this update that you referred to, again, this resulted from the exchange that Mr. DeVellis had with one of the panels.  I think it might be easier to explain once we get to one of the regulatory panels.

MR. VLAHOS:  Okay.  That's fine, sir.  I will wait for that.

In the meantime, the company may wish to refrain from filing those things again until we sort it out as to what they are, what they're supposed to represent, and what is the potential value for those things, because I'm sure intervenors who received that, they don't know what to make of it, and I don't know what to make of it right now.

The only thing I want to note is that, specifically on Tab 7 -- sorry, Exhibit B1, Tab 7, Schedule 1, Appendix "A", it is again a financial construct, a financial accounting construct.  It's not regulatory.  I don't know what its use is for purposes of this Board Panel, okay?  So that's the first question.

The second question is, again sticking with the blue pages, at the same time we had received Exhibit D1, Tab 2, Schedule 3, and that has to do with -- I don't know what it has to do with, other than Table 2, year ending December 2008, test dollar millions; and that's all I know.

There's nothing else here to help me as to what this is, other than to indicate there is an update to the services and meters number, which changes the total in service assets number.  But I don't know what to make of it.

MR. RODGER:  Yes, this particular one, sir, D1, Tab 2, Schedule 3, if you look to the right of the table, you'll see there's two "C"s, and this was to reflect changes as a result of the Smart Meter depreciation update that Mr. Jamal spoke to yesterday.

MR. VLAHOS:  All right.

MR. RODGER:  And that --

MR. VLAHOS:  So that was spoken to.

MR. RODGER:  That's right.

MR. VLAHOS:  That was just to update -- okay.

MR. RODGER:  That's right.  So there was an exhibit earlier in the week in a memo format that explained how the depreciation treatment changed, and now he's extended it further to show you how this one exhibit would be changed to reflect that update.

MR. VLAHOS:  I guess, Mr. Rodger, it goes to some of my previous questions.  Changing the depreciation on one line item, it would have a number of impacts on many lines of the prefiled evidence.

MR. RODGER:  Yes.

MR. VLAHOS:  That's why I fail to understand what is the significance of this specific update, as opposed to, why don't we take it all the way down to the revenue requirement change?

MR. RODGER:  Yes, I think that that latter change is the significant job that we'd spoken about earlier, that would take a number of days to flow it through the whole revenue model and ultimately into rates.

I think what these updates try and do is, as fast as the company can, make these changes we've talked about so the record will be more complete.  I think that's really the driver.

MR. VLAHOS:  And, believe me, I'm not the one who's going to suggest that you update your revenue requirement every time, by any means.  But at the same time, why the selectivity of just one exhibit as opposed to two or three or five?  I'm sure that depreciation expense will be in many, many documents in the pre-filed evidence.  That's why I fail to understand as to why we're doing it just on this schedule, and not others, and do we have to do it on this schedule as well, unless it comes up and somebody says, "Well, could you please update this?", in which case it will be an undertaking.

MR. RODGER:  I think with respect to this Smart Meter depreciation issue, the feeling was that it was a material change, and thus we would update the evidence accordingly.

For other very minor changes, we wouldn't do that, but I think this was one in particular that the company felt strong enough we wanted to provide the Board with first, a memo format explaining what had happened, and then update the particular page that dealt specifically with this cost item.

MR. VLAHOS:  All right, sir.

Finally, I guess there were two more exhibits that were filed by way of blue sheet updates.  D1, Tab 3, Schedule 2.

MR. RODGER:  Mm-hmm.

MR. VLAHOS:  I have updates to pages 1 out of 10, page 5 out of 10, and page 6 out of 10.  Let's stop there.

So there are three pages that were updated, and that exhibit is entitled "Distribution assets - variance analysis."

Can you help us as to the purpose of that update and no other?

MR. RODGER:  Yes, and it's the same response, Mr. Vlahos.  All these pages deal with the same Smart Meter depreciation issue.

MR. VLAHOS:  The same item?

MR. RODGER:  The exact same issue, yes.  We're just tracking it through the different documents in the prefiled evidence.

MR. VLAHOS:  And the same would apply for the update to Exhibit D1, Tab 14, Schedule 1?

MR. RODGER:  That's correct.

MR. VLAHOS:  No, I understand that now.  So are we now further ahead in terms of going forward what we need to update, whether anything?

MR. RODGER:  Yes.

MR. VLAHOS:  Mr. Chair, are you okay with that?

MR. SOMMERVILLE:  Yes, I think that's a very good caution, going forward, to ensure that if there are changes of a certain magnitude that sort of draw the interest and require updating immediately, in course, that's one thing.  But I think to go about this in a kind of fractured, piecemeal fashion is probably not a best way to go about it.

Mr. Faye, did you have any questions respecting the schedule?

MR. FAYE:  Yes, Mr. Chair, just a couple.

MR. SOMMERVILLE:  Just on the return of equity schedule.

MR. FAYE:  Yes.  Well, this is procedural, the first question.

QUESTIONS BY BOARD STAFF:

MR. FAYE:  We've entered this one.  This is the one

Mr. Vlahos was just questioning about return on equity.  But there's a second schedule attached to that, and

I don't believe it's been referred to in the record, so I just wanted to bring that forward.  R1, Tab 6, Schedule 17, Appendix "A" has been entered in the record as submitted.

MR. VLAHOS:  Yes, Mr. Faye, you're right, it was attached to my R1, Tab 1, Schedule 4.1.  So, yes, I guess the same discussion there.  Well, let me ask the --

MR. SOMMERVILLE:  Are these the underlying changes?

MR. FAYE:  Yes, and these are the filing requirements, and it's just again updated to reflect the same discussions on ROEs.

MR. VLAHOS:  So this is connected to the ROE update?

MR. FAYE:  Exactly.  Exactly.

MR. VLAHOS:  Does it also incorporate the depreciation expense change variance or not?

MR. SOMMERVILLE:  I wouldn't think so.

MR. VLAHOS:  All right.  So I guess the same would apply to this schedule as Exhibit R1, Tab 1, Schedule 4.1, Appendix "B", okay?   Those are the bottom-of-the-drawer documents?

MR. RODGER:  Yes.

MR. VLAHOS:  Thank you.

MR. RODGER:  And we do appreciate the Board's concerns.  What we're trying to do, as I say, if there is some material change that we think has arisen, we’re just trying to get the best information before the Board, understanding that you don't want changes for every single element of this many thousands of pages that may change.  So we are aware of that and we'll take that.

MR. FAYE:  A second question, Mr. Chair, on this, which I could direct to Mr. Jamal.

Looking at this schedule, and considering the discussion that's gone on here, I think everybody would like to see something that compares forecast retained earnings with Board-allowed retained earnings.  Is there somewhere in the evidence that we can make that comparison, or will you bring that forward towards the end of the hearing?

MR. JAMAL:  I believe that we are planning to update the amounts after all the discussions have been had.  The regulatory panel will be fielding that and processing the numbers, then we'll be issuing something after that.  I believe that was the plan, to do that after all the adjustments had been identified.

MR. RODGER:  Well, Mr. Faye, to be helpful; isn't that what's shown on this R1, Tab 1, Schedule 4.1?  It's the net income line, projected out to 2010?

MR. SOMMERVILLE:  I thought that Mr. Jamal indicated that this was not really a -- these two lines do not represent comparable figures.  And I took Mr. Faye's question to be the production of a document that does provide, on a common basis, the allowed return on equity and the actual return on equity.

My caution in this really goes back to the original interrogatory that asked for the percentage of actual return on equity, and it's not my interrogatory by any mean means, but just reading it, it looks at if what was asked for was the actual return on equity as a percentage, the allowed return on equity, and looking for the actuals, planned and projected.  I would have thought that what's needed now is production of that document on a common basis.

MR. VLAHOS:  And, Mr. Chair, that's why I have a difficulty with before, when I was asking the question, is that there's absolutely no reason beyond, in 2008 and after, to have any value other than this same value in the two circumstances.

I see Mr. McLorg is nodding there, so I guess maybe

I'm not too far off.

To the extent that the 2007 bridge, you know, the estimate may be different from actual to forecast, definitely for the historical year 2006 -- sorry, did I say '06?  2007, the bridge year, 2006, the actual year, there may be a difference between the actual and the allowed, and we understand the potential sources of that.

But going forward on a forecast basis, there's no reason why the numbers would be different.

MR. SOMMERVILLE:  I wonder if the way to get to this

-- and it may be that people take more than one shot to sort of get to this at the end of the day -- is to really understand the formulas that were used.  I'm assuming that the allowed return on equity is the formula that the Board uses.  That's the Board methodology.  And what might be helpful is to know precisely what the actual return on equity formula that was used by you in creating the original document.  If you can provide that, I think that may give us some help.  It may not be an end to the question, but I think it will be helpful.

MR. JAMAL:  May I answer that question?

MR. SOMMERVILLE:  Yes.

MR. JAMAL:  It's a standard accounting formula, that's net income divided by the average equity, shareholders equity of the company.

MR. SOMMERVILLE:  Okay.

MR. RODGER:  And I thought that part of the difficulty was bringing your actual figures into the regulated model.  I thought that was the problem.

MR. VLAHOS:  Yes, correct.  I might as well keep going back to my thesis, that it does not make sense to have those numbers side by side for the forecast period.  So I think everybody's agreeing there.  Mr. McLorg, are you able to advise your counsel there?

MR. RODGER:  I think we're agreeing with you.  I think all we're saying, Mr. Vlahos, is we did this to try to respond the best we could --

MR. VLAHOS:  No, I understand that.  I understand it.  But do we make anything more of it, or do we just stop here?  I thought we decided to just stop it here, okay?  So it is stopped here.

MR. SOMMERVILLE:  Well, I'd like to get the -- I guess we know what that formula is, and we'll -- I hesitate to say that it's stopped at this point, because the party who asked the interrogatory is not in the room at the moment.

The interrogatory, the original -- oh, it was.  Oh, I beg your pardon.  So I guess we are satisfied with the answers.  Is that fair, Mr. Faye?

MR. FAYE:  I think Board Staff, Mr. Chair, would like to see in black and white how this calculation was done, and if it's not too much trouble and they could give us an undertaking on that, it would probably satisfy Board Staff's confusion.

MR. SOMMERVILLE:  Sure enough.

MR. FAYE:  That would be T4.1.

UNDERTAKING NO. T4.1:  HOW THE CALCULATION FOR RETURN ON EQUITY WAS DONE.

MR. RODGER:  I'm warning you, Mr. Vlahos, this is another blue page coming.

MR. VLAHOS:  Oh, that's okay.

MR. SOMMERVILLE:  This shouldn't be a blue page.  This should be a white page.

MR. RODGER:  Okay.

MR. SOMMERVILLE:  This is not an update.

MR. VLAHOS:  I'm sorry, you're referring to the response to the undertaking?  Oh, no, we're going to go to pink now.

MR. SOMMERVILLE:  Mr. Faye?

CROSS-EXAMINATION BY MR. FAYE (Continued):

MR. FAYE:  Sorry, picking up where we left off just before the lunch break, I'll just remind everybody what the context of this was.  This is a discussion of a question that my co-counsel Ms. Campbell asked, and she was advised to ask this panel -- and it concerns Exhibit R1, Tab 6, Schedule 5, Appendix "A", which is this nice coloured chart -- of the number of full-time equivalents prospectively being added to Toronto Hydro, THESL, and how much of that could be attributed to the increase in the capital program.

Where we were at is that the response from the THESL panel is that, as usual, it's not quite so simple, and some things have to be removed.

What we got to is that civil construction is done by contract and not by Toronto Hydro forces.  And check my numbers on this, if you will.  I think you said that for 2007 about 20 million was attributable to civil construction, and for 2008 about 40 million was attributable to civil construction.

MR. LABRICCIOSA:  I think by 2010 it reaches 40, so it's scaled up.

MR. FAYE:  Okay.  But for the purposes of this sort of back-of-the-cigarette-package calculation I'm going to do here, this is probably good enough.

All right.  Now, if we take the schedule that I initially referred everybody to and asked to keep handy -- that is, D1, Tab 7, Schedule 1, page 10 -- this is the summary of capital budget.  I'm looking at the total distribution system line.

For the bridge year, it's 167 million.  We're going to take 20 off that, and we arrive at 147 million, and for the test year, 2008, it's reading 228.  We're going to take 40 off that and get 188.

Now, are there any other costs embedded in those two numbers I just came up with that really need to be taken out, that are not THESL in-house costs?

MR. LABRICCIOSA:  I think I'll draw your attention to a couple of points, in addition to the civil construction.  One would be Smart Meters.  It's a one-time type program, and although it's not just embedded in the 2008 test year, it does not show up in the previous years.  So it inflates the go-forward view and eventually drops off beyond the filing years.

The other matter I'll draw your attention to is, within metering, there is the ISO metering work, which is roughly 8 million in 2008, 10 million in 2009, and 7 million in 2010; rough numbers, again, which, again, are one-time expenses that are external to the company, related to market requirements.

And the last point I'll draw your attention to is, in the asset-management line, there is Hydro One contributions for, as identified, the Leaside to Birch project, and roughly, it's 5 million in 2008, 10 million in 2009, 20 million in 2010.

Once you extract those sort of round numbers, you're left with a view of what the type of work, the activity in the work program is all about.

MR. FAYE:  Thank you.

So I'm just going to look at 2008.  It just gets too confusing to try more than one year.

MR. LABRICCIOSA:  Sure.

MR. FAYE:  We were at 188.  We've taken 228, taken out 40 for civil construction.  Now we're going to take out 36 for Smart Meters, eight for the system operator, and five for Hydro One.  That's 13, 49, 137.  Do you agree?

MR. LABRICCIOSA:  Agree.

MR. FAYE:  Okay.  Now, what I want to do is compare that to the 2006 historical year, and that was 124.  And what we were discussing was -- what I thought you had said was that if we can set aside the fact that a lot of people are going to retire, and the fact that you're hiring apprentices, you seemed to imply that you would be able to handle this upswing in capital work that's evident between the two numbers that we're talking about here, 124 in 2006, and this one we just arrived at, 137.  There's about $13-million there.

Now, did I understand you right to say that your own forces would be able to handle that, because you were going to have programs in place that would promote better efficiency, more productivity?

MR. LABRICCIOSA:  In reality, we are adding staff, and you're honing in on the small adjustment numbers.

We are adding staff due to this plan.  So that is -- the 13 million roughly represents the increased effort required for this plan.  And, yes, we do have to add staff because of it.

But I'll also add, in addition to that, there is an expectation of some productivity improvement due to new processes, new systems, and skills upgrade that we're addressing with, again, people processing systems going forward.

MR. FAYE:  Okay.  Are you able to estimate what that number ought to be in a percentage term of productivity improvements?  Let's take -- we've got 13 million between the historical year and the test year that we're trying to sort of explain here.  Of that 13, how much would you say is going to be accounted for by better productivity?

MR. LABRICCIOSA:  I can't say offhand, sir.

MR. FAYE:  Okay.  Then I'm going to assume, for the sake of argument, that it's nominal.  Can I then conclude, coming back to where we started from -- this nice coloured chart -- that at least in 2008, at least 13 million of that budget, capital budget, is going to be consumed by the folks that you hire in that rising line?  And can I -- I'm sorry, I didn't get a response there.

MR. LABRICCIOSA:  Well, it is a balanced program, so that's the expectation that we have.

MR. FAYE:  And without going through this exercise for 2009 and 2010, can we say, by analogy, the numbers are somewhat similar, and so there's bound to be 13- to $15-million worth of capital work in those years that the people hired here are going to be involved in?  Okay.

MR. LABRICCIOSA:  The logic makes sense.  I will also caution you that we are also -- recall from the training perspective, there's a bit of a lag behind schooling, ramping up, setting up the program, setting up the resources, and getting them to a point to replace staff that are expected to leave as well.  So that's commingled in with that logic and conclusion as well.

MR. FAYE:  Yes, and I think where Ms. Campbell was going with this is, do you have the capability to do this capital program?  What I hear you saying, you know, we've just come up with a broad sort of number here.  Three years of roughly 15 million each.  $45-million has to be taken on by people that you don't have right now.  And now what I've heard you say is, the people that you're planning to hire aren't going to be able to do this work until they're trained.  Did I get that right?

MR. LABRICCIOSA:  Not necessarily.  I mean, that's a very -- that's a long leap in that conclusion.  They are doing work.  They are productive.  We're adding them in, but we're also adding them in in anticipation of retiring people as well.

So they are contributing.  They are contributing to the extra work that you've identified, in terms of that extended logic, but at the same time they will be replacing people leaving as well.

I just caution you that it's all mingled into these sets of numbers.  There's a human resource element, and then there's a capital element.  It's difficult to separate the two out.  I don't want to lose train of thought that they -- we haven't built these plans in separation.

MR. FAYE:  No, I appreciate that this is probably considerably more complex than I'm trying to make it, because we're trying to deal with it in fairly simple terms here.

I understand also that as you go through your apprenticeship program, those individuals get more and more productive.  Each year they can do more, I think; is that correct?

MR. LABRICCIOSA:  That's correct.

MR. FAYE:  So the effect of the training starts to mature towards the end of if 2010 test year.  All right.

I think that's all I have to ask about that, subject to Ms. Campbell instructing me to pursue it any further.

So, with that, I have one more follow-up question and then I can get to my actual cross-examination, and this has to do with a Pollution Probe question that I'd like clarification on.

I think you said, in response to one of their questions, that the ten-year capital expenditure plan amounted to 1.17 billion.  I just wonder if I got that number right, or did I misunderstand what you were saying there?

MR. LABRICCIOSA:  I did say subject to check, and I'm going to check right now.

--- Witness panel confers.

MR. RODGER:  I believe, Mr. Faye, was not the question -- did it not relate to sustaining capital?

MR. FAYE:  That was going to be my next question.

MR. LABRICCIOSA:  Yes.  Just to clarify, in our submission, the ten-year capital plan, which I believe is Schedule 10 of D1, Tab 8, and I'm going turn you to page

13.  There's a table, table 6, and, again, for sustaining capital requirements in this plan, it's 1.17 or 1,170 million, or 1.17 billion.  I did have it right.

MR. FAYE:  Thank you.  That clears it up.  I was unclear as to whether it was sustaining capital or total capital, but if you say it's sustaining capital, then the amounts being spent in each of these years is relatively one-tenth of it.  Thank you.

I'm looking again as this schedule of capital, D1, Tab 7, Schedule 1, page 10.  We already talked about some of the numbers here.  I would just like to get some confirmation on the record of what these numbers are.

Starting with the 2006 test year to 2007, we're going from 213 to 157, and by my calculation that's about a 35 percent increase.  Would you agree with that, subject to check?

MR. LABRICCIOSA:  I would.

MR. FAYE:  And following up on that one, 2007 to 2008, it appears that there's an increase of about 81 million.

Again, that's about 38 percent.  Would you agree with that?

MR. LABRICCIOSA:  I would agree.

MR. FAYE:  And comparing 2006 expenditures to that

2008, the difference is about 137 million.  I calculate that to be about 87 percent.

MR. LABRICCIOSA:  That's correct.

MR. FAYE:  Would you agree with that?  Now, between

2008 and 2009 the increase slows down, and it's only about 7 million between those two years, about two and a half percent.  But between 2006 and 2009, the increase is

144 million, and I make that to be about 92 percent.  Do you agree with that?

MR. LABRICCIOSA:  I would agree with it.

MR. FAYE:  Finally, between 2009 and 2010, the expenditure increase between those two years is only 9 million; again, about 2.9 percent.  But, comparing to 2006, the increase is 153 million, and that translates into about

97 percent.  You agree?

MR. LABRICCIOSA:  That's correct.

MR. FAYE:  Now, turning to the first subcategory, "Sustaining capital."  Could you give us a brief description of what distinguishes that section, that category, from the next one?

MR. LABRICCIOSA:  In the sustaining capital, it's strictly distribution equipment, and it's strictly dealing with equipment that's in place today, that is deteriorating, aging, and at the end of life and underperforming, that needs to be replaced.

MR. FAYE:  And contrasting that with some of the work that's noted in the second, ignoring things like capital contributions, engineering capital, but focussing on reactive work, what's in reactive work that wouldn't be up above?

MR. WONG:  I will try to answer that.

Reactive work is the work that we do to try to restore the grid to its normal state after an emergency-type failure.

MR. FAYE:  So it's unplanned work?

MR. WONG:  It's unplanned.  It's demand-driven.

MR. FAYE:  Would it be fair to say that the sustaining capital section is planned work and the reactive stuff, customer connections, you really just are responding to demands placed on the system that you don't have much control over?

MR. WONG:  Correct.

MR. FAYE:  Okay.

Then, looking at the sustaining capital in a little more detail, the underground direct buried category is the first one.  I wonder if you could describe how you develop your expenditure plans in that category.

MR. LABRICCIOSA:  How the projects are identified is a function of both the inventory we have of underground direct buried cables -- so we've split that out as a portfolio, sort of an asset class -- and we look at performance of those assets, historical performance, which pinpoint areas of the grid that require the attention, and our assessment then becomes is it a one-time anomaly or is it a trend?  And if it's a trend, it becomes a long-term investment plan to replace, because again, the situation being at end of life.   And so projects are extracted from that review process, and categorized and defined more distinctly into particular specific project units.  Then plans are developed to execute on that plan.

MR. FAYE:  Am I right in assuming that that's what you refer to as your asset management plan at various places in the thing?

MR. LABRICCIOSA:  That's correct.

MR. FAYE:  Could you just elaborate a little bit on when this asset management plan was first developed?

MR. LABRICCIOSA:  It stems from the 10-year capital plan.  I mean, that is the asset management plan for sustaining capital.  There are parts and pieces -- we'll stay with underground direct buried cable.

During the course of these reviews, in the particular case of cable, as we identify specific instances where cable is failing, we begin to look at: is it an anomaly or is it an actual trend?  When we actually identify it being a trend, we go back into sort of study mode to figure out, well, what's causing this trend?  And the reason why I'm sort of spending a little time here:  We submitted John Densley's cable analysis from our system, so we asked somebody to help us through understanding what's happening with that cable.

And once it's confirmed that it is at the end of life, and validated, then we begin to look at the areas that are failing in terms of performance, and then that really starts to form the genesis of the plan, the steps that we take to replace it.

So we go with the highest outage area, highest outage frequency areas, and start divvying up those areas as projects, and that forms what we call a scoping package in the planning process.

We begin to scope out these areas, and put estimates together.

Once we've defined a geographic area and how far and deep we want to go with the replacement, we develop a project estimate that eventually goes into construction.

What you see in front of you, in terms of the filing, is the project estimates that have been defined in that process.

So the estimates really reflect a detailed plan, execution plan, that has to go out into construction.

MR. FAYE:  Okay, so I understand that that's the application and your methodology.  I think maybe my question was:  When did you develop the methodology that you're using?  This asset management planning tool thing?

Does that go back to the origins of Toronto Hydro or is it something that came in after amalgamation?  That's what I'm getting at.

MR. LABRICCIOSA:  I've only come into my role and responsibility within the last year, so I can't really comment exactly when it came into play.  I have been with the company quite a long time, and we've always had this aspect of asset management, in terms of a process.

I would say it's not as rigorous or detailed as I've defined it at this stage, or as mature, but we've always had this view of looking at assets that are performing poorly, and then doing further study in terms of determining whether it's a one-time issue or if it's a trend, and then once we've confirmed it being a trend, to develop a parsed-out or segmented plan around replacement.

MR. FAYE:  One element of that plan, I think I hear you saying, is reliability.

MR. LABRICCIOSA:  Correct.

MR. FAYE:  Is that right?

In the course of that plan, do you attempt to reconcile or draw a balance between what you're trying to get reliability-wise and what effect it's going to have on your customers' rates?  Is that a consideration in that process?

MR. LABRICCIOSA:  I wouldn't say we draw those two endpoints together with a straight line, in terms of so many dollars, or so many dollars of rate impact are reflected in reliability performance.  I don't think we look at it that way.

I think there is a loosely coupled link there, in terms of what projects are necessary to keep reliability in check.  Eventually, it defines the dollar investment needed to do that, which eventually links back to rates.

MR. FAYE:  Mm-hmm.

MR. LABRICCIOSA:  So if your question is, is there a direct link, do we look at rate impact and reliability, I don't think we do that directly, not in the asset management plan.

MR. FAYE:  Okay.  Then do you do it at some other point in your planning process?

MR. LABRICCIOSA:  I think at the end of the day, once we put all the plans together from a budget perspective, as part of our planning cycle in our company -- I think Mr. Couillard talked about that budgeting cycle -- there is a rate analysis done at the very end.

MR. FAYE:  And if there tends to be rate shock as a result of the plans, do you revisit the plans and try to come up with some other -- you know, extend them, whatever?

MR. LABRICCIOSA:  In my short tenure we haven't done that.

MR. FAYE:  All right.  So it sounds like the capital budget is driven by what your asset management plan assesses as a need, and primarily to maintain reliability, and you've picked some target band for reliability.

MR. LABRICCIOSA:  Correct.

MR. FAYE:  Okay.  Thank you.

I'd like to go now to the notion that in 2006, if I heard you right, this sort of planning was in place at the time.  It hasn't just come out last year.

MR. LABRICCIOSA:  Correct.

MR. FAYE:  And the results of that planning are significantly different than the results in the test years, and in the bridge year, for that matter, in terms of how much capital you're going to invest.

Can you elaborate a little bit on what happened in your planning process that changed the outcome so dramatically in the test years?

MR. LABRICCIOSA:  In looking back, I think what we can say is, even if you go pre-2006, you'll notice the level of spending for capital refurbishment is typical of 2006 or lower.

I think what you can say is, while we were -- while we had invested in a system years before that, we were maybe riding a bit of a wave of complacency, in terms of the system.  We've invested it in previous years.  We're still riding its performance.

The performance has not been catching up to that investment until the last couple of years, in terms of, we've noticed that the system is deteriorating, and as we have failed to keep up with that replacement, we've now realized that the performance is not going to come back without major capital investment.

So one might argue -- I can only speculate, looking backwards -- that we either -- we're taking a very short-sighted view, and we're comfortable with the performance we were getting and the state of our system.  But recently, having had a look at it through an asset-condition assessment and re-evaluating our performance and the condition of our system, we've realized that it's at the end of its life.

MR. FAYE:  Okay.  I think you've presented some evidence that, you know, seeks to support that situation.  I'd like to take you to this first consultant's report that you commissioned; and this is the Kinectrics study, and it's in Exhibit D1, Tab 8, Schedule 9, Appendix "A". That's another one you might want to keep out, because I'll be referring to it a couple of times.

So I'll just ask you some general questions on that while the Panel gets their copies out.

Can you tell us who Kinectrics is?

MR. LABRICCIOSA:  Kinectrics is a company that came about or as a result of the divestiture of Ontario Hydro into separate companies.  It used to be Ontario Hydro Research Labs, as one of a group of departments within Ontario Hydro, located on Kipling Avenue.

As it broke out, it broke out under its own entity, known as Kinectrics, and I believe they've been bought out entirely by a separate company.

MR. FAYE:  So it's a private corporation?

MR. LABRICCIOSA:  It is a private corporation today.

MR. FAYE:  Now, I'm sure the reason you put this in here is that you would like them to be recognized as an expert opinion on the condition of your plant; is that right?

MR. LABRICCIOSA:  That's correct.

MR. FAYE:  Can you tell us why you think that they are experts in this?

MR. LABRICCIOSA:  They have conducted similar work for other companies.  Hydro One, namely, is another company that they've done work for in this umbrella.  And I believe they do have a reputation worldwide for research in the power industry itself.  So --

MR. FAYE:  Would you consider them, for instance, to be experts in utility management?

MR. LABRICCIOSA:  Utility management?

MR. FAYE:  Yes.

MR. LABRICCIOSA:  Asset management, yes.  Works management, probably not.

MR. FAYE:  Okay.  Design of systems?

MR. LABRICCIOSA:  Yes.

MR. FAYE:  You think that they could -- you could call them up and contract out your urban design for subdivisions?

MR. LABRICCIOSA:  That may be a bit of a stretch, but I would think that if you look at the components used in that design, I think they're experts in that.

MR. FAYE:  Okay.  They have lab facilities, do they?

MR. LABRICCIOSA:  I still think they run a lab on Kipling Avenue.

MR. FAYE:  And they do what's referred to in this report, forensic testing of components?  Do they do that sort of thing?

MR. LABRICCIOSA:  That's correct.

MR. FAYE:  Has THESL used them for that kind of service?

MR. LABRICCIOSA:  We have in the past, in terms of poles, pole strength, cable testing, cable-failure analysis.

MR. FAYE:  Okay.  Now, they're a for-profit entity.  They're in business to make money.  They make money by testing failed components, as I understand it, and they're rendering an opinion on which components are at risk in your system.  Do you see any conflict there?

MR. LABRICCIOSA:  No, sir.

MR. FAYE:  You would consider them to be completely independent?

MR. LABRICCIOSA:  Yes, sir.

MR. FAYE:  Okay.  When did you get the report back from them?

MR. LABRICCIOSA:  The report is dated Friday, February 2nd, 2007.

MR. FAYE:  Do you agree with the analysis that Kinectrics has undertaken and the recommendations they've made?

MR. LABRICCIOSA:  I would agree with it.

MR. FAYE:  Have you taken any steps to implement the recommendations?

MR. LABRICCIOSA:  We have taken some.

MR. FAYE:  Could you elaborate on which ones?

MR. LABRICCIOSA:  I believe we've provided that in an interrogatory.  If you would give me a second, I can pull that back up.

MR. FAYE:  Okay.

--- Pause in proceedings.

MR. LABRICCIOSA:  I'm going to point you to Exhibit R1, Tab 2, Schedule 10.  It's Energy Probe's interrogatory.  I believe the question is similar to what you asked:

"What is THESL's response to each of the recommendations arising from the Kinectrics report as listed in Section 6?"

MR. FAYE:  Can you just go through that briefly?

MR. LABRICCIOSA:  Sure.  The first response, and I guess it's in the order of recommendations made in the report:

"THESL has initiated a review of the health indices to include a more comprehensive indication of condition."

And essentially, we're in the midst of that work.   Some of that work has been stalled to date, due to some of the work we had to put together with the rate filing.  But we still anticipate that it will be done by the end of 2008.

With respect to the second recommendation, which is:

"A risk assessment should be conducted to prioritize the assets that require replacement."

We've referred to another exhibit in the schedule.  I think it's a Consumers Council of Canada, under D1, T8, S1.  Schedule 1.

On the third recommendation:

"The health index formulation for the asset classes for which the audit found a significantly poorer than average condition need to be re-examined and possibly reformulated."

Again, we point to another interrogatory response there, and it's related to D1, Tab 8, Schedule 9.

On the need for re-examining circuit breakers, our response there was:

"THESL as part of the review being conducted in 1 above will be directing information to enable a more granular examination of non-homogeneous asset classes like circuit breakers.  And specifically, circuit breaker data will be collected so that the specifics of each interrupting type -- that is, oil, SF6, gas, aeromagnetic, et cetera -- will be captured."

In the fifth recommendation, it was looking at failure modes of assets, and trying to classify and evaluate them and incorporate them into maintenance programs.  And our response there was:

"Asset failure modes have been identified through THESL's reliability-centred maintenance analysis.  The maintenance strategy support system is currently being developed in Ellipse in order track those failure modes."

Ellipse is our ERP, enterprise resource planning system.  In that system, it includes an asset management module, and failure-mode tracking is part of that module.  We're in the midst of implementing that.

The sixth recommendation:

"Further study is required to gain an improved understanding of the condition information of underground cables."

In our response, it's referencing the response in Exhibit R1, Tab 3, Schedule 31, for the types of assessments on cable condition.  In addition, again, as part of Ellipse, we have a linear asset-tracking module that we're looking to implement.

In Densley's report, and I referred to that a couple of times, it talked about exploring the use of non-destructive testing, and that's the acoustic pickup methodologies for trying to look at arcing of cables and using arc sound to predict the performance of the cable.

And, again, with us being tied up with this rate filing, we have yet to follow up with that particular work, but we intend to do so.

And the last recommendation:

"Statistics should be gathered on age at which assets were replaced in the past, and why they were replaced."

Our response is:

”The tools being developed in 5 above --" and again, that's the maintenance tracking system --"will be used to address this recommendation.  THESL has decided to focus on improving its condition-based assessments."

And that would be the response.

MR. FAYE:  Okay.  Thanks.  Of the seven, we have number 1: there's going to be a review of the health indices system to sort of fine-tune it.  That will be completed in 2008.

Number 2, risk assessment: you referred us to another exhibit.

Number 3, health index formulation: disagreement, possibly, with other systems, I think you could categorize that as.  That's been referred to another exhibit.

Number 4: you're going to collect some more data to get better granularity.

Number 5, understanding the failure modes: you're collecting that in your reliability data management system.

Number 6, further study to gain an improved

understanding of the condition of your underground cable: you've referred us to another exhibit there, and maybe that's one of the ones I'll ask you another question on.

And you've mentioned the Densley report.  And number 7, stats gathered at the age at which assets are dying: and you're starting to collect that, although you haven't had enough time to put into it.

MR. LABRICCIOSA:  Mm-hmm.

MR. FAYE:  Before we go further, let's concentrate a bit on number 6:

"Further study is required to gain an improved understanding of the condition information of underground systems."

That suggests that there's some doubt in the conclusion that cable systems need replacing; and the secondary conclusion I draw is that the projects included in your capital budget are based on inadequate information, if you compared it to this recommendation.  Is that a fair assessment?

MR. LABRICCIOSA:  I wouldn't draw that conclusion.  I would say, in parts of the ACA, it does talk about, there is good data for underground cable and station transformers, which corroborate the levels of investment we're making.  So it's based on good data in terms of what they concluded in their analysis.

I think what it does say is underground cable is a linear asset, so there's quite a bit of it in the ground.

There's a significant investment being made.

You want to take a closer look at how you prioritize those investments, a lot closer than what we possibly have in terms of data today, so that you have it in the right sequence and order as opposed to looking at such a large volume at once.

So the takeaway I have is, collect more data to help stratify your investment better in a sequence of priority, as opposed to drawing the wrong conclusions on the data is inaccurate.

MR. FAYE:  I could see where that could be an interpretation of it, but if you look at recommendation number 5, it says:

"There is a need to further understand the particular failure-mode of assets on the THESL system, in order to ensure that replacement programs are truly warranted, and not the result of a reparable condition."

It sounds to me that your consultant is telling you you need more data before you can draw broad conclusions about cable replacement programs.  Is that a reasonable interpretation of this?

MR. LABRICCIOSA:  I wouldn't necessarily say on cable.

I think, again, more data is helpful, to help determine the exact timing of that investment.  But I think that statement also couples to all the other asset classes, and there are some we did not have specific data for, or enough data for, and we had to rely on the age-based methodology to develop the 10-year plan.

MR. FAYE:  Yes.  So if you're relying on age-based methodology, that's not as legitimate, do you think, as -- that's probably not the right word.

MR. LABRICCIOSA:  Right.

MR. FAYE:  It's not as good as a reason to replace it as if you had a health index; is that what you're saying?

MR. LABRICCIOSA:  I would say it’s not as helpful an in-depth analysis as a health index, that’s correct.  And age could be used as a proxy for replacement.

MR. FAYE:  Yes, but what I hear you saying, it's not a real good proxy.

MR. LABRICCIOSA:  Again, I think we're claiming to be a company that is progressive, and getting better at how it does its work and gets better going forward.

I think asset managers in general, in terms of evolving in the future, it's evolving with better analysis, better data, better results, better decision-making.

I would say it's not a fixed plateau that you achieve; it's one that you continually evolve and get better at.

MR. FAYE:  I guess I'm still a little confused.  If you have full condition assessment of your cables, then presumably you know; you know, in detail, how bad they are.

And if you don't have that, then you have these other proxies.  One is age.

What I was asking is:  If all you've got is age, are you less confident in the cable condition than you would be if you had partial discharge testing like mentioned in some of these reports and that sort of thing?

MR. LABRICCIOSA:  Yes, I would think some methods would lead to a stronger conclusion around end of life, performance.  But I'd also caution you to say performance is also a good indicator as well, albeit it's a lagging indicator or a reactive type indicator.  But that will also confirm, along with age, that assets are at the end of life.

MR. FAYE:  Okay.  Turning to, then, the way you have constructed your cable-replacement program, I'm thinking particularly of the direct buried cable, because that seems to be where you have the most problems.

What did you base those replacement programs on?  Is that based on age?

MR. LABRICCIOSA:  Are you referring to the projects in the plan?

MR. FAYE:  Well, you have a summary here on this one I keep referring to: underground direct buried.  I'm assuming that that is the sum of all the projects that you've submitted?

MR. LABRICCIOSA:  That is correct.

MR. FAYE:  And those projects, are they based on an analysis that is founded on age of the cable?

MR. LABRICCIOSA:  No, I think you'll notice in some of the -- in the age study, or in the age review, the age of that particular type of cable was not available, or was not accurate enough to solely base a determination of age alone, in terms of a record.

So I would have to say it's both age, performance, and condition.

MR. FAYE:  Okay.  Performance, you're measuring from your reliability indices; is that right?

MR. LABRICCIOSA:  That is correct.

MR. FAYE:  Condition, how are you measuring that?

MR. LABRICCIOSA:  From this work that was done by Kinectrics.

MR. FAYE:  And did Kinectrics actually go out and test your cables?

MR. LABRICCIOSA:  In some cases, they did a field audit, which corroborated their conclusions.

MR. FAYE:  The field audit was some of these forensic or diagnostic testing procedures?

MR. LABRICCIOSA:  I don't think they took samples of the cable back to the lab and did a strength or breakdown analysis.  I think they just went out and looked at concentric neutral corrosion condition in the field, did a visual inspection.

MR. FAYE:  Okay.  And where in your system, considering that it's direct buried now, where do you get to see that sort of thing?

MR. LABRICCIOSA:  Well, when it comes into a pad-mounted vault location, you peek at the face of the vault.

MR. FAYE:  Okay.  So you can see the part of the cable that you've referenced as a concentric neutral, and if it's corroded at that point, you assume it's corroded all the way down the cable?

MR. LABRICCIOSA:  That's a strong assumption.

MR. FAYE:  Okay.  Nobody did any connecting of instruments or sending any pulses down the cable that would give them an indication of a particular section, how bad that cable was?

MR. LABRICCIOSA:  No, you're correct in that.

MR. FAYE:  Okay.  Is it always the case that if you have corrosion on the concentric neutral, that the rest of the cable is necessarily in danger of failing?

MR. LABRICCIOSA:  Not always the case, but it is a symptom.

MR. FAYE:  So in summary then, it sounds like, at least for the direct underground buried part, you have taken into account age and a visual inspection of what would necessarily be a very limited part of your system, simply where the cable comes out of the ground and you can see the end of it.

MR. LABRICCIOSA:  That's correct.

MR. FAYE:  And are you confident that that gives you sufficient information to base a capital program on that is in the $50-million range?

MR. LABRICCIOSA:  Yes, we are.

MR. FAYE:  Are you planning to undertake any diagnostic testing to confirm that?

MR. LABRICCIOSA:  Not to corroborate this plan, no.

MR. FAYE:  And why wouldn't you do that?

MR. LABRICCIOSA:  This three-year plan is really addressing our poorest areas.  It's addressing those assets that are poor and very poor.  In most of these cases, we're dealing with outages of 12 times a year.

So we could spend a lot more time researching.  But I would say with fairly good confidence that we have a tiger by the tail in this particular case with underground cable; that we have to go out and replace it.

MR. FAYE:  Okay.  You do collect statistics on how cable failed?

MR. LABRICCIOSA:  We collect failure statistics; correct, yes.

MR. FAYE:  Okay.  So --

MR. LABRICCIOSA:  The mechanisms of failure?  Is that what you're leading to?

MR. FAYE:  No, what I'm getting at is, when you get a call-out because the cable has failed and people are out of power -- someone's got to go out and dig it up and fix it -- do you know how many instances that is for failure of a splice, for instance?

MR. LABRICCIOSA:  We do collect that information.  We trend it.

MR. FAYE:  Yes.  And do you have information on how many splices have failed?

MR. LABRICCIOSA:  We collect splices and cable failures.  We distinguish between the two.

MR. FAYE:  Okay.  And how do they compare, numerically?

MR. LABRICCIOSA:  I don't have that data in front of me, but it is cable failures, not splice failures, we're addressing here.

MR. FAYE:  So you're confident that you have no, you know, sort of generic faulty splices in your system that could explain your cable problems?

MR. LABRICCIOSA:  Correct.  You know, I think the industry as a whole in the past, given my history, there were workmanship issues and equipment issues with respect to pre-moulded splices and hand-taped splices that would lead to a great deal of splice failures.  But I think we grew out of that through the '80s and '90s.  The predominant failures we're experiencing right now are not splices, but cables.  Cable.

MR. FAYE:  Then in summary, I guess what I'm hearing is, age of cable is a criterion that you use to identify an area that might be problematic, and within that, you look at reliability statistics to see how many outages you've had on the cable, and then you prioritize them according to the impact of an outage, I'm assuming, and list out your projects; and that's your plan?

MR. LABRICCIOSA:  That's correct.

MR. FAYE:  Does diagnostic testing take a lot of time?

MR. LABRICCIOSA:  For underground cables?

MR. FAYE:  Yes.

MR. LABRICCIOSA:  It's not necessarily the time that we'd be concerned with, I think, in some cases.  It's the impact to the system.  So to do the testing, it would be de-energized.  To de-energize it means you put -- you load other cables that are at the end of life, higher than what they are, in which case you're exposing them even further in order to test segments.

Again, we'd be looking for non-destructive energized testing, and I don't think that environment, that sort of realm of testing, has matured yet.

MR. FAYE:  You're suggesting that it's unreliable?

MR. LABRICCIOSA:  I don't know that there are any techniques yet that are around that make it both pragmatic and reliable, in terms of results.

MR. FAYE:  All right.  Well, let's take, for example, one of the projects that you have.  It's an underground subdivision, and you want to replace all the cable in there.

In order to test that cable, am I right in saying that you would have to go transformer to transformer?

MR. LABRICCIOSA:  Correct.

MR. FAYE:  Okay.  So in order to do that and take it out of service to do that, how many customers would you have on two transformers -- or one transformer, is what it amounts to?

MR. LABRICCIOSA:  Anywhere from 15 to 30 customers could be on that transformer.

MR. FAYE:  All right.  So you could take an interruption on that leg of conductor.  You could do your test.  15 to 30 customers would be inconvenienced.  15 to 30 customers' loads, would they be picked up from some other place?

MR. LABRICCIOSA:  Sure.  They'd have to, I would think.

MR. FAYE:  How would you do that?

MR. LABRICCIOSA:  Well, in a loop system, you just transfer them over to the other part of the loop, so you do segment by segment, so I'm assuming if that's -- that if that's the example you're using --

MR. FAYE:  Fifteen to 30 customers are going to be put on the rest of the loop?

MR. LABRICCIOSA:  The adjacent loop.

MR. FAYE:  The adjacent loop.  Okay.

And are you suggesting that that 15 to 30 customers would impose such a burden on that adjacent cable that it would experience a failure or would be put in jeopardy?

MR. LABRICCIOSA:  It would burden the cable, double than what it would be normally.  So that's one element I would describe it as.

The other is, you know, the situation you're describing, you're testing 30 metres of cable or less, 15 metres of cable.  So there's a lot of 15-metre cable segments that make up an entire subdivision, so it becomes, again, impractical to do it segment by segment.  But it's possible.

The other element I'll add to it is, again, if you know that the cable is at the end of its life, so the age is there, the performance is telling you that it's tenuous, and, you know, you've had field audits confirm -- albeit not the entire length of that cable -- but confirm conclusions drawn by a paper analysis that was done of the records, I would question whether we would actually want to go out and do that on every one of the projects we've listed.

MR. FAYE:  Well, I guess where I'm driving at, of course, is if it's possible to replace just the bad parts of the system --

MR. LABRICCIOSA:  Mm-hmm.

MR. FAYE:  And if you can determine which are the bad parts, by diagnostic testing, it would seem to make some sense to invest the time and money involved in that, rather than not only costing yourself a lot of money in capital, but inconvenience your customers by digging up their whole street.

So I'm wondering, if you have a tool available, according to the Kinectrics reports, I think it's not an expensive tool -- I think they quoted something like $5,000 a day that this service was available for.  I think they even quoted something in the neighbourhood of $400 per cable section for testing it.  Given that the unit costs of replacing this stuff seems to be in the $500 a metre range, I'm wondering why you wouldn't put $400 into a test before you committed to spend a huge amount of money to replace cable that may not need replacing.

MR. LABRICCIOSA:  Oh, no, it will need replacing for sure.  I think what we're talking about is, again, stratifying that investment.

I'll respond in two parts.

One is this cable is at the end of its life, so you might push it out for six months, so it is somewhat of a stranded investment.  Perhaps you've replaced it a couple of months early.  You said it makes sense to do that?  I don't think so.  You need to replace it.  Period.

The other element is the costs you've quoted were the

Kinectrics costs to rent the equipment.  We didn't talk about all the set-up costs in order to isolate the pieces of equipment, so if you're trying to do 100 kilometres of cable 10 metres at a time to test it out, that's going to take quite a long time to do, and it's going to involve a lot of isolation work in order to do that, so it's not a question of $400 or $500.

Add to that all the work to isolate, and the inconvenience to the customers in terms of the outages, and we're talking quite a bit of effort and inconvenience.

MR. FAYE:  I note that we started out that these transformer segments were 35 to 40 metres, and now we're going down to 10 metres apart.  That means there's one at every house in Scarborough?

MR. LABRICCIOSA:  Could be.  You know, I might have been generous at 45.

MR. FAYE:  Can I take you, then, to -- I'll give you a moment here -- Exhibit R1, Tab 3, Schedule 25, Appendix "A".

MR. LABRICCIOSA:  Did you say Appendix "B" or Appendix "A"?

MR. DeVELLIS:  Appendix "A".

MR. LABRICCIOSA:  "A".

MR. DeVELLIS:  This is the study report on direct buried cable in Toronto Hydro distribution system.

MR. LABRICCIOSA:  Correct.

MR. FAYE:  Now, this has been prepared by your own  staff, I'm assuming?

MR. LABRICCIOSA:  That's correct.  Mr. Kahn works for us.

MR. FAYE:  If you look at the top of page 7, first paragraph, I'll read it:

"In the residential subdivision, a single-phase transformer feeds 10 to 15 houses.  Transformers are spaced between an average of 400 metres."

Is that an incorrect statement in there, or a mistake?

MR. LABRICCIOSA:  I think the analysis he did was in his area.  That's what he looked at.  But I'll take it that he's correct in his analysis.

MR. FAYE:  So that would vary from your assumption of even 35 to 40 metres by an order of magnitude.

MR. LABRICCIOSA:  It doesn't represent the entire system.  I think that was just done in a particular area.

MR. FAYE:  But you do have areas where transformers seem to be spaced 400 metres apart.

MR. LABRICCIOSA:  Absolutely.

MR. FAYE:  Okay.  And so to bring in a diagnostic testing program for that, you would be testing 400 metres.

MR. LABRICCIOSA:  Sure.

MR. FAYE:  So I'd ask you once again, if it costs $400 to test that section, and at $500 a metre, my quick math would say you're going to spend $200,000 replacing that cable -- does it not make sense to do a few 400-metre sections and to see if they're good or bad?

MR. LABRICCIOSA:  Again, your cost on that doesn't include the effort used to isolate and set up for the tests.

MR. FAYE:  No, I recognize that you do have to do some switching in order to isolate transformers.  But your trouble crew does that all the time, I'm sure, doesn't it?

MR. LABRICCIOSA:  Again, in responding to cable failures, yes.  But once the cable's failed, there's no use testing it at that point.

MR. FAYE:  No, I agree, but you certainly have the capability to do this, and it's not an unusually onerous task.

MR. LABRICCIOSA:  Yes.  But again, your question or your comment related to:  Does it make sense?  No, it doesn't, not on cable at the end of life.

MR. FAYE:  But I think we're getting into a little circular reasoning here.  The whole push purpose of a diagnostic testing program is to determine whether the cable is at the end of its life, and you haven't done that yet.

MR. LABRICCIOSA:  What we filed in front of you is the evidence that shows what our conclusions are and that it is at the end of life.

MR. FAYE:  And that conclusion is based on age of the cable, a review of reliability statistics, and a visual inspection of some parts of the system that Kinectrics did in conjunction with their study?

MR. LABRICCIOSA:  That's correct.

MR. FAYE:  And you would still maintain that that's a sufficient basis to develop a replacement program that approaches $1.1-billion, and you don't plan to undertake any further testing?

MR. LABRICCIOSA:  For cable, I believe what we're putting in front of you is close to $100 million, and it's only for the first three years.  I would concede the point to you that I think as time goes on, we probably have better -- we need better methodologies or better methods to test the remaining parts of the plan in order to create the strata necessary that we deal with those in worse condition than those that are in better condition.

And that would be part of our plan, as noted in the recommendations in the Kinectrics report and some of the work that we're proceeding with, going forward.

MR. FAYE:  And so, does that mean you are going to implement some sort of diagnostic testing program?

MR. LABRICCIOSA:  I think you're right.  We started off in that interrogatory response.  We're in the midst of doing some of that work, and we intend to do that.  It's just we don't have that result today.

MR. FAYE:  Mr. Chairman, I'm going to move to another subject, at least another section.  If you want to take a break, this would be a good time.

MR. SOMMERVILLE:  Seems reasonable.  We will reconvene at 3:15.  Thank you.

--- Recess taken at 2:59 p.m.

--- On resuming at 3:18 p.m.

MR. SOMMERVILLE:  Thank you.  Please be seated.

Mr. Faye, you were cross-examining.  It would appear as though, perhaps, Mr. Faye, you could advise me that this panel will probably have to return on Monday morning?

MR. FAYE:  I think at the pace that we're going, yes; I don't think we're going to finish by 5:00.

MR. SOMMERVILLE:  Does that create any particular difficulties?  Let's pick a convenient -- if we're going to go over until Monday in any event, pick a convenient break, so that you're not sort of stuck in between issues, so if you have to deal with an entire subject matter on Monday morning, that's better than splitting it over the weekend.  Thank you.

MR. FAYE:  Where we were at before the break, we were just sort of finishing up with this issue of what underlies the replacement of all these cables and the justification for it.  And I think we can just summarize by saying that in the report of distribution capital, D1, Tab 8, Schedule 1, page 8 -- if you could turn that up.

MR. LABRICCIOSA:  Sorry, Mr. Faye, can you repeat that again?  Sorry.

MR. FAYE:  That would be Exhibit D1, Tab 8, Schedule 1, page 8 of 26.

MR. SOMMERVILLE:  This is the Kahn report?

MR. FAYE:  This is distribution capital.

MR. SOMMERVILLE:  I beg your pardon.  Thank you.

MR. FAYE:  Have you got that?

MR. SOMMERVILLE:  Yes.

MR. FAYE:  I'm reading at the top of that page, just underneath Table 3:

"THESL used two key criteria to assess the circuit areas in need of replacement, and those two criteria are the number of failures per unit length of installation and the age of each direct buried cable."

I'm assuming that's an accurate statement?

MR. LABRICCIOSA:  Yes.

MR. FAYE:  And I think I'll finish off this part of the questioning just by asking you, prior to the Kinectrics report, what did you use as your basis for replacing cable, direct buried cable?  Was it age of the circuit, number of failures per unit length?

MR. LABRICCIOSA:  Probably the latter, failures per unit length, prior to this submission.

MR. FAYE:  Okay, and at the time that you were using that, the amount of cable that you were replacing was a lot less than what you are proposing to replace in the test years?

MR. LABRICCIOSA:  Again, it's hard for me to comment on how far back you want to go.  It's definitely less, but I would -- it's hard to quantify a lot less or --

MR. FAYE:  Well, as an example, we could just take the 2006 historical year.  It was 7 million there.  It's 31 in the bridge.  It's 45 in the first test year.

Just comparing to 2006, when you used this criteria as well, the conclusion you drew at that time was that you had to spend 7 million?

MR. LABRICCIOSA:  Right.

MR. FAYE:  Now, using the same criteria, the conclusion is you've got to quadruple or quintuple that amount.

MR. LABRICCIOSA:  That's correct.

MR. FAYE:  Okay.  Thanks.

I'd like to turn you to the ArborLek report, and that's at Exhibit R1, Tab 3, Schedule 25, Appendix "B".  Got that?

MR. LABRICCIOSA:  Yes.

MR. FAYE:  Can you just give us a quick run-down on why you commissioned this kind of study and report?

MR. LABRICCIOSA:  Again, we felt that, given the trends we were facing in terms of performance and our look at the age of cable and the amount of cable we had in the ground, our own analysis pointed to a problem area, and we felt that we needed an outsider's perspective on it.

And Mr. Densley -- and I've referred to him a couple of times -- is regarded as a cable specialist in the industry, so we sought out his advice at that time.

MR. FAYE:  All right.  When did you get this report?  I didn't see a date on it, so I'm curious as to when you commissioned this and got it.

MR. LABRICCIOSA:  2006.

MR. FAYE:  2006?  And do you agree with the analysis and recommendations of this report?

MR. LABRICCIOSA:  Yes.

MR. FAYE:  Has THESL taken any steps to implement the recommendations?

MR. LABRICCIOSA:  Some.

MR. FAYE:  Would you describe those to us?

MR. LABRICCIOSA:  I'll turn you to the conclusions page of the report.  Some short-term actions they recommend -- if I read them off to you, is that all right?

MR. FAYE:  Sure.

MR. LABRICCIOSA:  And tell you, sort of give you a state-of-the-nation in where we are with some of these?

MR. FAYE:  That would be great.

MR. LABRICCIOSA:  "Consolidate the databases from six former utilities into one database."  I referred to some of the Ellipse references and the systems that we were using to do that.

"Collecting cable accessory/age."  We're in data-gathering mode, and we're putting a plan together as we go forward to have field staff collect data and populate the fields that we've created in our systems to capture and house the data.

Talked about "the lengths of different types of cable installed each year."  There was a reference to GEAR earlier, and that's our geo-spatial mapping type system.  Since we are finishing that project, we now have one database, mapping database, where we can capture accurate lengths and start to label it with the type of cable, the age, those kinds of elements.

Looking at "examining alternatives to soldering, lead wiping to repair PILC cables," that's lead cables.  We're experimenting and looking at heat-shrink type components that are out on the market.

"Continuity of cable crews by maintaining a good apprenticeship program."  A lot has been said about our trade school, one of which carries this trade and prepares this group of entrants in the organization, the underground joiners and mechanics, for this type of work, and it supports the apprenticeship that we do there, the internal apprenticeship program that we have there.

The next bullet talks about "forensic program could be part of an EPRI ECTN program."  I think what he's referring to, EPRI is a research -- Electric Power Research Institute, a company out of the States, that could do some forensic analysis.  We have yet to explore that at this point.

Again, I've mentioned it a couple of times.  The better part of this year has been spent compiling these -- this filing and putting this information together.  This is one of those to-do items that we still have to explore.

In the long term, there are a couple of items in there that we have in the works: the development of electronic failure reporting from the field, the development of in-house statistical cable replacement model.  I think that speaks to your point of testing, gathering data and developing a model for projecting end of life or predicted failures.

And then the diagnostic program: again, I don't think we've done anything there, but we have that on the radar of things to do.

MR. FAYE:  Thanks.  That was very, very helpful.

If I could just go quickly through them again, number

1 involves an IT system.  That's what this Ellipse system is, and I think we'll talk about that when we get to the IT capital.  There's some data-gathering going on for recommendation number 2, the lengths of cable.  It sounds like you're going to be able to extract that from this automated mapping system called GEAR.  Did I get that right?

MR. LABRICCIOSA:  That's correct, and it's part of the amalgamation.  We had six different systems come together, and they work to varying degrees in terms of the type of functionality they are provided.

So different levels of data and support came together, and had to be merged together, and we have missing data in some systems and good data in other systems, so it's not complete across the city.

MR. FAYE:  I think you missed "restore the feasibility of using EPR cables."  What are EPR cables?  Are they some super-duper cable?

MR. LABRICCIOSA:  It's just a different compound of dielectric, so it's still the same -- you know, they are considered somewhat plastic cables like XLPE.  It's just a different technology of cable manufacturing that's used.

MR. FAYE:  Do you think that this would make a significant difference to your cable performance, using this particular type?

MR. LABRICCIOSA:  We have not studied it, so it's hard for me to tell.  I think in the materials I've read, I would liken it to the advent of technology that we went from lead cables to cross-linked cables.  The jury is still out on which is really the best cable in the system.  This is another one of those leaps of technologies or modernization.  EPR is relatively new in terms of coming to the market, and so I think the jury is still out on whether it's better, in terms of performance and longevity, than cross-linked polyethylene.

MR. FAYE:  Okay.  The next one involves maintaining the internal capability to actually handle cable, and you say your apprenticeship program is addressing that.

The forensic program you haven't explored yet, but do I hear you making a commitment to undertake some forensic investigation of cables that have faulted, or components that have faulted?

MR. LABRICCIOSA:  We have to do that.  Yes.

MR. FAYE:  (Reading)

"Possible higher failure rate in accessories with jacketed extruded cables should be investigated to see if it's a problem with cable crew training."

Can you explain what that means?

MR. LABRICCIOSA:  I believe this point refers to some problems we've had historically in the industry with extruded jacketed cross-linked polyethylene cables, and the workmanship in preparing the cables for terminations, as well as installing them in the system.  And if, for instance, the workers cut too deep, cut back the insulation too far, it created problems; so it was more of a workmanship issue than it was a product issue.

It was a newer product, which required a different skill set in training to handle, and so I think what he's referring to is to ensure that we've crossed that point in time, and I think we have.

MR. FAYE:  These cables are not the ones that we're

customarily talking about in your direct buried program?

MR. LABRICCIOSA:  That's correct.

MR. FAYE:  These are other ones, more modern cables, and there was a small blip in failures there that caused them to focus on this?

MR. LABRICCIOSA:  That's correct.

MR. FAYE:  Okay.  You're going to develop an electronic reporting form; and automatic entry to the database, joining EPRI and joining their cable asset management program is not under consideration at the present time?

MR. LABRICCIOSA:  I think that was a plug by John in terms of putting a bit of a program forward that he believes in personally, in trying to promote it.  We haven't considered it or dismissed it, but we think it's something we can push a little bit back in terms of decision point.

MR. FAYE:  And the next one, "development of an in-house statistical cable replacement model," is that along the same lines?  EPRI's not noted there, but I wonder if --

MR. LABRICCIOSA:  I think, Mr. Densley does some work with other utilities.  Progress Energy is one of these utilities that we interact with for exchange of best practices and information, and I think he's referring to some of the work they did in modelling their system, and using their models to project failure rates or end of life points in cables.

MR. FAYE:  And the last one, the diagnostic testing program, what I think I heard you say was you haven't got it yet but it's on the horizon, and you expect this to yield some better data around cable condition?

MR. LABRICCIOSA:  Yes, and, again, I'm going to come back to some of the points you raised earlier -- Mr. Densley referring to part of his long-term strategy, or long-term effort -- and again, given the situation we're in today, yes, we do have to do this, but it does not solve what we're facing today, with our Phase I of our ten-year capital plan, which is the immediate replacement of cables that are imminently failing out there.

MR. FAYE:  Can I turn you to page 33 of that report?

MR. LABRICCIOSA:  You will have to help me.  I don't think my pages are marked on this one.

MR. FAYE:  Oh, I'm sorry.  I had to mark my own.

You're right.  This particular report does not have pages.

That would be -- how far back -- the conclusions page that we were looking at is page 49, so you want to be back about 16 pages from that.

MR. LABRICCIOSA:  Cable life extension?

MR. FAYE:  The top of that page has a square box.  The first word in it says "accessible."

MR. LABRICCIOSA:  Does it say accessories?

MR. FAYE:  No, accessible, and then "risk of inducing damage to cable during tests that might cause failure."

MR. LABRICCIOSA:  Okay.

MR. FAYE:  So, in this section of his report, he's talking about testing of cables.

In the paragraph just following that boxed comment on sort of consequences of tests, he says:

”Partial discharge tests can be carried on-line or off-line."

So that suggests that you can do this with the cable alive.  Is that how I should understand that?

MR. LABRICCIOSA:  That would be the general sense of that point, yes.

MR. FAYE:  And if we skip down to paragraph number 4:

"On-line testing does not require an outage, although a utility crew is usually present during the testing."

Do I take it that to mean that the cable can be tested alive in that situation too?

MR. LABRICCIOSA:  Yes.

MR. FAYE:  Okay, and so you've mentioned previously that not all the costs are in here.  He does say that the typical cost per cable is 400, and you have to add to that the cost of your standby crew here, because it's being performed live; I understand that.

MR. LABRICCIOSA:  Mm-hmm.

MR. FAYE:  All right.  I just wanted to confirm that.

MR. LABRICCIOSA:  But I do think, if you read further on, it's D.T. Proben is the company that has developed this technology.

MR. FAYE:  Yes.

MR. LABRICCIOSA:  And they were the only ones doing it at the time, and I do believe other utilities have put together materials that show that -- put it this way, that draw a different conclusion on the reliability of that test.

MR. FAYE:  The reliability of the test done on a live cable as opposed to a dead cable?

MR. LABRICCIOSA:  Using this method; that's correct.

MR. FAYE:  Okay.  I'll take your word on that.

If you could flip forward a few pages to page 43.

The caption at the top of the page is "Cable life extension techniques."

At the bottom, it looks to be the last two sentences of that paragraph:

"Localized neutral corrosion can be repaired, but general corrosion over a considerable length of cable can become a safety concern, and the cable should be replaced."

Previously, I asked you about the visual inspection, and you've given evidence that someone could open up a transformer and look at the cable where it's terminated on the transformer, and from there you can see these concentric neutral wires all grouped together and see if they're corroded.

But you can't necessarily conclude from that, that that corrosion is continuous down the cable, can you?

MR. LABRICCIOSA:  That's correct.

MR. FAYE:  Are there conditions in that transformer case that might cause corrosion in there and not cause corrosion anywhere else?

MR. LABRICCIOSA:  Could be situations like that, yes.

MR. FAYE:  So I'm thinking of, in submersible vaults, subject to road salt and runoff, same thing.  If a pad-mount transformer is sitting right beside the road and a salt truck is going along, throwing salt all over everything, it gets ploughed up by the snowplough.  So there are some situations that almost lend themselves to corrosion inside your transformer cases, right?

MR. LABRICCIOSA:  I guess I would agree with you, but I'd also agree with you that it's part of the conditions of the whole environment.  So it's not only that, you know, it's exposed to that contaminant or that exposure within the vault; it's exposed in the soil.  It's the runoff.  Everything, you know, everything; it affects the installation, I would say, quite uniformly.

MR. FAYE:  Yes, I would agree that there are other factors, but I'm only trying to get at, in this case, that if someone lifts the lid on a pad-mount transformer and looks inside and sees corrosion on the neutral wire, is it sensible to conclude, just from that visual inspection, that that corrosion has somehow travelled down the cable and undermined the neutral all along the cable?

MR. LABRICCIOSA:  It's possible.  I wouldn't say, again, that -- unless you inspect the entire cable, it's inconclusive at that point, I would suspect.  What we're trying to do is draw an analogy that if it is extensive, in terms of exposure to the environment and age, given that corrosion is oxidation, which is really exposure to elements, that if part of the cable is extensively damaged, it's likely damaged throughout.

MR. FAYE:  I think that was the purpose of that question.  I think I heard you agree that conditions inside a transformer case and in submersible transformers are such that you could get localized corrosion, simply because it's exposed to salt from the road and other environmental contaminants, and that the rest of the cable is buried.  It's underground three feet, and not subject to the same exposure.

MR. LABRICCIOSA:  But you also have to keep in mind, Mr. Faye, that we also do maintenance on that equipment.  So it does see maintenance activities, cleaning, so on and so forth, whereas the rest of the cable does not.

So there, you're right, there are other factors that do come into play.  You know, if your line of questioning is around absolute certainty, then I'd have to agree with you.  You cannot be absolutely certain until you actually expose the whole thing.

I think what we're trying to do is draw an inference and some logical conclusions that lead you to believe, given the age, the condition, and the environment that it's installed in, that it would lead you to believe that it is at a stage of life that is corroded and end of life.

MR. FAYE:  Okay.  I take your point.

Moving on to the following page, at this point Mr. Densley is talking about alternatives to replacing cables, and I wonder if you could just give us your opinion on these methods that he's suggesting here; that is, injection of cables with a silicon compound.  That appears to be a viable technology from reading his paper, but I'm no expert.  What do you think of that?

MR. LABRICCIOSA:  If you're -- I'm going to assume we'll disregard the PILC dialogue around heat-shrink and the 3M- and Tyco-type sleeves that are used there and focus on the last part of it, which is really around cross-linked cable.  Is that okay with you?

MR. FAYE:  Yes, go ahead.  If I have any objections, I'll note them.

MR. LABRICCIOSA:  We are exploring the use of cable injection going forward right now.  In fact, we are working with two different companies on a pilot basis to determine the effectiveness of this type of rejuvenation.

This is not new technology to the industry.  We've explored this in the past in our other companies, and there are people inside our company who are familiar with it.  I think they go back as far as 15 to 20 years in the industry, in terms of cable injection.

What has changed from then to now is the workmanship required to do the rejuvenation.  We are experimenting with it right now to see if it's a better alternative, rather than replacement at this stage.  We don't know enough about it at this point to draw a conclusive point or direction on changing the capital program.

MR. FAYE:  Okay.  I understand, though, that you said it's been around for 15 to 20 years, so it's not a new technology.  There's lots of data available on how long those cables that were treated 20 years ago have lasted?

MR. LABRICCIOSA:  Some have failed.  The conclusions drawn in the past in those experiments by those companies -- again, I'm only going by the reports, not firsthand knowledge.  They dismissed the technology at that stage.

MR. FAYE:  I'm sorry, could you just repeat?  Why did they dismiss the technology?

MR. LABRICCIOSA:  They've dismissed it in terms of it's not cost-effective.

MR. FAYE:  Not cost-effective.  And yet in the middle of the second-to-last paragraph, I see your consultant says:

"Most utilities justify the use of rejuvenation based on the 40 percent to 50 percent savings, compared to replacing with a new cable, and that they've had good experience with cables that have been rejuvenated for at least 18 years."

Are you suggesting there is more current information that would discount that conclusion he's drawing there?

MR. LABRICCIOSA:  No, I think what he's saying is probably factual and correct, depending on the utility applications and the conditions for which they have done the work.

I recall, again going back in time, Orange and Rockland Utilities in the U.S. had experimented with this technology, were very promoting of the technology at one point, and no longer do this any more.

So again, given more information that comes to light, each utility draws its own conclusions.  I think some utilities do find it cost-effective, given whatever situations they've based themselves in.  In our particular case, if I go back to our old companies, two utilities that did explore it, dismissed it.

MR. FAYE:  Okay.

MR. LABRICCIOSA:  But we are looking at it again to see if it has changed and it would be cost-effective for us to consider.

MR. FAYE:  I think in the context of such a huge capital budget, any alternatives to trying to do that kind of work in the time period you're predicting it can be done in might be prudent; if they can be spread out over a larger number of years by using some of these techniques, that that might be a more satisfactory solution than burdening your ratepayers all in the course of a few years.  Would you agree?

MR. LABRICCIOSA:  I think you have a very positive statement in there, and I'll draw that statement into a direction we're taking.

We have a problem right now.  The first three years deals with cables that are at the end.  We are experimenting with these technologies to prepare for the next phase, so that's really years 3 through 7, and as we update our plan, we will fold these conclusions going forward into that part of the plan.

In essence, we're sort of running in parallel here.  We can't afford to do this in sequence, determine whether technology is mature and reliable enough today to use that going forward, and then, if it doesn't, then do capital rebuild.

We have to do our capital rebuild now, but we also have to be mindful and keep our eye on evolving technologies and revisit even older technologies that have changed, to see if it still can be tapped into our program.

So I would see the results of this work folded into years 4 through 10.

MR. FAYE:  Okay.  I think the last comment I'd like to draw out on this report is the last paragraph, and it suggests that there are some technical remedies, if you will, that can be applied to limit the amount of damage done, if I understand them correctly, when you do get a fault or when you do get a lightning strike, that can degrade the insulation and lead to earlier failures.

He mentions one, surge protection at both ends of the cable circuit.  Can you just describe for the Panel what that means?

MR. LABRICCIOSA:  I think what Mr. Densley's referring to is, some utilities, especially in the States, have higher occurrences or higher isochronic levels, higher occurrences of lightning strikes.  Up here in Canada, our isochronic level is relatively low in contrast to, say, Florida, so we have not explored this particular protection scheme for us, at this stage, because we do not see a lot of lightning strike-induced failures in our underground cables, although he points out that it can protect your cables going forward.

MR. FAYE:  All right.  Thanks for that.

I'd like to turn you now to Exhibit D1, T8, S10.  This is your 2007-16 Electrical Distribution Capital Plan.

MR. LABRICCIOSA:  Yes.

MR. FAYE:  Got that turned up?  Could you look at page 8, under "Underground cable XLPE direct bury."

The number over in the right-hand column is 777.  And

if you then flip to page 12, a similar presentation; near the bottom, "Underground direct cable buried."  And the number is 2321.  I wonder if you could explain for the Panel why those numbers are different.

MR. LABRICCIOSA:  The first table that you reference, which is table 2, when we presented that table, we presented it in circuit kilometres, so every circuit in the system is mapped with -- it generally has three cables to a circuit, although there are some circuits that could have two or possibly one.

So it measures cable in circuit kilometres.

Table 5, which is your page 12 reference, identifies cables by conductor kilometres, so in essence every individual conductor is measured.

MR. FAYE:  Is your budget proposal founded on this number for underground direct buried?

MR. LABRICCIOSA:  It is founded on the conductor kilometre.

MR. FAYE:  Conductor kilometre.

MR. LABRICCIOSA:  That's exactly how we replace it.

MR. FAYE:  And I heard in your explanation to the Panel that cable systems can be three-phase, in which case there are three conductors.  They can be two-phase, in which case there are two, and they can be single-phase, in which case there is one.  There's none that can be four-phase; right?

MR. LABRICCIOSA:  No, we don't use that.

MR. FAYE:  So if I multiply three times 777, I get very close to this number, 2361.  Not exact; in fact, this number is a little larger.  I actually get 2331, so the number in this chart is actually a little larger than you would arrive at by assuming every circuit was three-phase.  But I think I've heard you say, not all circuits are three-phase, and they're certainly not more than three-phase, they're less.

And so I'd like to ask you why that hasn't been factored in.  Why do you take such a large number, rather than factor in the number of two-phase and single-phase circuits?

MR. LABRICCIOSA:  It really is a function of the accuracy of our underground records.  I talked earlier about our GEAR systems, and there are legacy systems from the six independent companies, so bringing them together, we're at a stage now where we're trying to become more accurate with the information that we have.

It's a function of referencing two data points that we have.

MR. FAYE:  Okay.

MR. LABRICCIOSA:  That would be the inaccuracies between the two.  We don't have the magical fourth phase or we have, you know, more cable in one system than we have in the other; strictly inaccuracies between the systems we use.

MR. FAYE:  Okay.  But would you agree that the inaccuracy results in overstatement of the amount of cable that really needs to be replaced?

--- Witness panel confers.

MR. LABRICCIOSA:  It's very hard to say over or under at this point in time.  It is inaccurate.  But we feel confident if it's not inaccurate by magnitudes of 10, it's inaccurate in terms of the last kilometre or series of kilometres, so if we said plus or minus 5 or 10 percent, I think we'd be okay.

MR. FAYE:  Okay.  Well, it certainly can't be plus, not based on the analysis -- if 777 is the correct number, then the very maximum it could be is 2331, because you multiply it by 3.

Would you agree it can't be more than 2331, unless the 777 number is wrong?

MR. LABRICCIOSA:  Again, I would say there is some level of inaccuracy between the two.  It's not a strict multiplication by three to get one to the other.

MR. FAYE:  Right.  Yes, and I guess what I'm trying to get at is sometimes it's a multiplication by one, and sometimes by two, and sometimes by three, but never by four?

MR. LABRICCIOSA:  Right.

MR. FAYE:  So the net result is, if you come up with that number by multiplying by three, the inaccuracy is overstated, not understated?

MR. LABRICCIOSA:  Well, again, it's data that's coming from two systems.  We're not trying to equate them.  It's just information we're extracting from both sides.

MR. FAYE:  All right, and you're relatively confident that it's within 5 to 10 percent; did I hear you say that?

MR. LABRICCIOSA:  We haven't quantified the error, but, again, our records shows there's cable exists out in the system.  When we go there, the system may say it's 400 metres.  When we go there, it might actually be 390, and so -- or 420; and, again, it's by route, as opposed to by roadway.

Some utilities did not necessarily use a transit system to mark the path of the cable, the direction or the route of the cable.  Others just went by, you know, roadway kilometres and didn't necessarily reflect where the route of the cable went, so that's where some of this error comes from.

MR. FAYE:  Can I turn you back, then, to the Kinectrics report.  That's at D1, Tab 8, Schedule 9, Appendix "A".

I'd like you to look at page 7.  There's a chart there, and the first two entries in the chart are "underground feeder cable direct buried,"  "underground distribution cable direct buried."  And then if I look down through the rest of the table, I don't find anything else that says "direct buried."  I see some stuff in "duct." But if I add together the first two categories, if you look under the "Population" column, if I add 300,000, and 1,188,000, I get 1,488,000 metres, or 1,488 kilometres.

Would you agree with that?

MR. LABRICCIOSA:  Mm-hmm.

MR. FAYE:  Could you explain why that number varies so much from the 2361 number in the capital plan?

MR. LABRICCIOSA:  Again, I believe the answer to that one would be circuit kilometres versus conductor kilometres, whereas the work done in the ACA or the asset condition assessment, was done in circuit kilometres -- circuit kilometres, correct -- and the work done in the THESL ten-year capital plan is conductor kilometres.

So what you're seeing is the population in circuit kilometres.

MR. FAYE:  So if we use the three-times rule, would you then say that we're looking at a total population of about 4.3 kilometres?  Three times 14 is 4.2, plus a bit?

MR. LABRICCIOSA:  Again, that's an approximation.

MR. FAYE:  But it's double what you have in your plan.

Why would that be?

MR. LABRICCIOSA:  Again, when you look at it, again, circuit kilometres, it's just one method of collecting data.  As we mentioned before, some feeders are actually -- or some delivery points are single conductors.  I don't think you can do a strict multiplication of the two to get the number.

I would say I would say conductor kilometres is the more accurate figure, what we have in our plan.

MR. FAYE:  That you've arrived at by multiplying 777 by 3?

MR. LABRICCIOSA:  No, I didn't say that.  I kept telling you, we extract data from two systems.  One system has conductor.  Another has it in circuit.  So --

MR. FAYE:  Can I turn you, then, to a Staff report that we've looked at previously, and I believe it's at R1, Tab 3, Section 25, Appendix "A".  This is the study report on direct buried cable.  I'm looking at page 2.

MR. LABRICCIOSA:  Correct.

MR. FAYE:  The second chart on that page appears to list all of the different types of cable and how much of them there is in the system, and it comes to, the bottom number, 1,489.  It seems to agree very closely with the number we've just seen in the Kinectrics report.  Would you agree with that?

MR. LABRICCIOSA:  The numbers do match.

MR. FAYE:  Would you think that's coincidental?

MR. LABRICCIOSA:  No, sir, I don't know if that's conductor kilometres or circuit kilometres.

MR. FAYE:  No, I agree; it does not specify.

MR. LABRICCIOSA:  Right.

MR. FAYE:  I think the point I'd like to make is that in one place your capital plan relies on one number, and there's other evidence here that is radically different.  Whether it's conductor kilometres or circuit kilometres, it's different by an order of 2.

I think there's some parts of that chart that would indicate to you that it's single-phase, for instance triplexed conductor.  That would be secondary, would it?  Or am I misunderstanding?  Is that -- does the "TR" refer to triplexed or tree-retardant?

MR. LABRICCIOSA:  No, that's tree-retardant, sir.

MR. FAYE:  Okay.  So there's no way of telling from this whether these lengths are conductor or circuit?

MR. LABRICCIOSA:  I would tend to believe -- and I'll do it subject to check if you like -- that it would be circuit kilometres.  I would take exception to your point that, you know, the data we presented here is inaccurate.  I think there are some inaccuracies, as I've mentioned, but not to the point where they're double or triple, factors of 2 or 3, levels of inaccuracy.

As I've pointed out before, the THESL capital plan, conductor lengths in kilometres, reflect what we know about the lengths of cable in our system today, and that's the one we're using going forward.

The circuit kilometres in the ACA is data we submitted to a third party, not necessarily coming from the same systems, as well as the report done by Mr. Khan, is again an extrapolation from a different database.

We are confident, with the THESL capital plan in front of you, D1, Tab 8, Schedule 10, that that is a best reflection of what we know about the system today, with a relatively high degree of accuracy that we're working with, given our history.

MR. FAYE:  And it's arrived at by inspecting your electronic maps of the system, and doing some sort of -- if it was a physical map, you would have a little wheel that measured things off, but on an electronic map, the electronic equivalent?

MR. LABRICCIOSA:  Sure.  What we've done is, in the process of converting our maps to one common platform, the GEAR platform, which we have -- we are just finishing now or have just recently completed, depending on how close we are to the end of the year -- we're pretty much at the end of it now.  The information that we have now is more accurate, based on that one system.

MR. FAYE:  Okay.  And so what you have done is added up -- had your computer add up everywhere where you know there is cable, and so you have a route length.  And then you've made some assumptions to convert that into conductor length.

MR. LABRICCIOSA:  Correct.

MR. FAYE:  And what were the assumptions you made there?

MR. LABRICCIOSA:  Again, when you say "assumptions", we've looked at the characteristics of the route being -- it's either three-phase or single-phase.  If it's single-phase, it's one cable.  I guess the assumption on the three-phase is there's three cables in there.  There are some cases where we have three-conductor cable, which is really one conductor -- or three conductors, one piece of cable.

So maybe it's a complicated answer to the question.  I'm just not sure where you're going with that.  In that case, we call that the replacement, when we put it in three different ducts, which we would do in some cases.  We would call that length-three, because we have to replace it with three pieces of conductor.  In some cases we replace that with one conductor again, or one run with three conductors embedded into one jacket, and we'd call that one.

MR. FAYE:  Okay.  So I think, in summary, what I'm hearing is, even though it was THESL that supplied Kinectrics with the data that they used, you're not confident in Kinectrics' 777-kilometre figure, right?

MR. LABRICCIOSA:  Again, I keep coming back to, it was data we pulled out of a system that measured in circuit kilometres, and that's the way they've handled it.

MR. FAYE:  And presumably someone, Mr. Khan, used the same system and got this 1,489.  Have you used some other system, then, to come up with your 2,361?

MR. LABRICCIOSA:  Again, when we look at 2,361, we're referencing a common system platform from the GEAR system and using that data.

MR. FAYE:  And that data originated in six separate systems?

MR. LABRICCIOSA:  Six separate systems, held by each utility, prior to amalgamation.

MR. FAYE:  And so when you gave Kinectrics information, did you go to those six systems and get it out of there and then send it over to them?

MR. LABRICCIOSA:  I can't really comment on how we did that.  I'd have to go back and ask exactly how we pulled that data together.

MR. FAYE:  But it would be a reasonable assumption that --

MR. LABRICCIOSA:  Sure.

MR. FAYE:  -- you wouldn't have missed one system.  You would have got all six.

MR. LABRICCIOSA:  Sure.  They'd have to go to some level of system, whether it's actually hardwired -- or hard-coded maps, mapping information, or the other system.  Some utilities did not have a geo-spatial type mapping system.  They just had a schematic-type mapping system, where, in fact, the actual routes, cable routes, were held in physical hard maps.

MR. FAYE:  Okay.  Before we leave the Staff report here, could you just take a look at the top of page 7?  I think I've read you the first sentence here before, when we were discussing the distance between transformers.  I'll read it again:

"In a residential subdivision, a single-phase transformer, 50 to 167 kVA, feeds ten to 15 houses.  Transformers are spaced between an average of 400 metres.  Assuming an average of 13 houses, with 11-and-a-half-metre service from the roadside, including the stretches along the road, cables, there will be about 150 metres of secondary spur cables off the primary cable route along the roadside for every 400 metres of primary cable."

Do I understand that to mean that there's more primary cable in a residential subdivision than secondary cable?

MR. LABRICCIOSA:  I'm not sure I can draw the same conclusion as you.  I think that just sort of rep -- those statements talk about the lengths of wire within a subdivision that feed homes versus that feed the transformers there.

MR. FAYE:  It seems to be fairly clear.  It says here's 400 metres of cable between transformers if they're 400 metres apart.  That's primary, and that sounds sensible.  You would need the cable to actually reach the next transformer to make it connected.

MR. LABRICCIOSA:  Mm-hmm.

MR. FAYE:  And then it says there's 150 metres of secondary.

MR. LABRICCIOSA:  Mm-hmm.

MR. FAYE:  But is that a sensible conclusion?  Is it your experience that there's less secondary cable in a subdivision than primary cable, typically?

MR. LABRICCIOSA:  Again, it depends on the areas.  I'd have to take a look at the 400-metres statement that we've made there.  I mean, that seems very long, from the subdivisions I know.  Ten houses represent about 40-metre frontages on that.  So I think those are pretty exclusive homes, if I look at it that way.  So I'm not sure that 400 metres is correct.

MR. FAYE:  Okay.  In general, would you agree with the conclusion that there's usually more secondary cable than there is primary cable?

MR. LABRICCIOSA:  I would say as a general statement, that would be fair.

MR. FAYE:  I'd like to turn to the costs associated with cable replacement, and while we're still on this report, look back on page 6, and you'll see in that bottom chart 1490 kilometres at $600, and I'm assuming that $600 is per metre.  And he comes up with an estimate of $894 million to do that replacement.

MR. LABRICCIOSA:  Mm-hmm.

MR. FAYE:  So, keeping in mind $600 per metre here.

Now, if we can go back to the Kinectrics report.  On page 7, in that chart that we were looking at on conductor lengths.  "Underground feeder cable direct buried," 500.

MR. LABRICCIOSA:  Mm-hmm.

MR. FAYE:  And "Underground distribution cable direct buried," 280.  These are, again, costs per metre, I take it?

MR. LABRICCIOSA:  Correct.

MR. FAYE:  I'd like to take you to a schedule that we looked at a little earlier, if I can find it here, and that is an interrogatory from the Schools, Interrogatory No. 27.  It's Exhibit R1, Tab 5, Schedule 27.  Have that turned up?

MR. LABRICCIOSA:  Yes, I do.

MR. FAYE:  I refer you to the table on page 2 of that interrogatory, the response, and looking at "three-phase feeder" in the top box, the entire cost -- again, per metre, I'm assuming -- is $500.  Would you agree with that?

MR. LABRICCIOSA:  In the first box, total unit cost, the bottom left-hand corner?

MR. FAYE:  Yes.

MR. LABRICCIOSA:  Correct.

MR. FAYE:  And if I look at the bottom box, "Distribution three-phase," comparable figure in 2006 is $323.  So per kilometre, that would be 323,000, and I'd like to suggest to you that the top box, 500, seems to correspond very closely with the Kinectrics study that we just looked at for the top entry in their table, 500 per metre.  But the second entry in their table was 280, if I recall, and I'm comparing that to this 323.  And I wonder if you could comment on why there would be such a difference between those two numbers.

MR. LABRICCIOSA:  I would suggest to you, sir, that the table that's concluded in the interrogatory is the more accurate.  It has the breakout of material, labour, vehicle.

MR. FAYE:  Well, while we're on these tables, could you tell us what is in the other category in each of those breakdowns?

MR. LABRICCIOSA:  Could be a variety of costs outside of material, labour, and vehicle.  One could be contractor costs.

MR. FAYE:  Could that be the cost of a civil contractor to put in a reinforced duct bank?

MR. LABRICCIOSA:  Yes.

MR. FAYE:  Okay.

MR. LABRICCIOSA:  Could also be the cost of pulling in just a direct buried duct.

MR. FAYE:  Okay.  Thank you.  Would there be significant costs other than that cost?  Can you think of any?

MR. LABRICCIOSA:  It could also include restoration, depending on the extensiveness of the restoration involved in the neighbourhood.

MR. FAYE:  Can I conclude from this that, looking at these figures, 0.250, compared to the total, it's about 50 percent.  The next box down in "Other," 110, compared to 220, it's about 50 percent.  And similarly, in the third box, 0.162 is about half of 0.323.

So 50 percent of the costs is in the other category, and is it fair to assume that most of that is civil work, concrete encasing and that kind of thing?

MR. LABRICCIOSA:  I would say it's a fair assumption at this stage, at the high level.

MR. FAYE:  Then can we turn to some of the other alternatives, then, one of which you just mentioned, a direct buried duct.

If there's significant costs in reinforced concrete structures, do you gain some measure of reliability and protection for your cable and save some money if you don't put the concrete in?  If you just put in a duct and, you know, put the sand on top of it, how does that compare with a reinforced concrete structure?

MR. LABRICCIOSA:  Well, obviously the concrete encasement provides, I guess, the mechanical protection of the cable, probably the ultimate mechanical protection in cable, in contrast to cable and duct, and in contrast to direct buried cable.

MR. FAYE:  Okay.  So if, for instance, you're going to cross a road, and you have buses down there and heavy traffic, as, you know, forcing frost down, I think I would agree with you that there's some sense in building reinforced concrete structures.  But I'm wondering, in a residential subdivision, where you're in the front lawn of customers and you're crossing underneath their driveways, well, that's about the worst exposure you're getting.  I'm wondering why you would go to the extent of putting in a reinforced concrete structure in that case, why you wouldn't just butt a direct buried duct system in there.

MR. LABRICCIOSA:  Again, we wouldn't necessarily put a reinforced concrete system underneath a driveway, per se.  In some cases, depending on the nature of the subdivision, regarding the requirements of occupying the boulevard allowance and what the City mandates in terms of the place where we have to comply in terms of their road allowance.  In some cases we're forced to put in a concrete-encased or an unshrinkable fill environment, or some specifications that require stronger mechanical protection other than direct buried duct or direct buried cables.

So in some cases, we have no choice.  In other cases, we do have a choice, and when it comes to that choice, I guess it's a judgment on our part, depending on, again, a lifecycle analysis.  When you look at a duct bank, for instance, if a cable fails in a duct bank, you pull that section of cable out.  You alluded to that earlier; you know, maybe you could just replace a section at a time.

A duct bank will allow you to do that and will house maybe three generations of cable, as opposed to one.  Those are the kinds of aspects we consider whenever we look at an area, a replacement in an area in an underground subdivision.

So I wouldn't say definitely every case calls for a concrete encasement.  I would say we'd consider it, and depending on the situation, we would use that or we would use the alternative, which would be direct buried duct.

MR. FAYE:  Of the projects that you have listed in the binders here, have you customarily used direct buried duct in residential subdivision applications?

MR. LABRICCIOSA:  I believe in some of those projects they are direct buried duct.

MR. FAYE:  Okay.  Thank you.

I think I heard you mention in one of the intervenors' questions that the method you propose to employ in reconstructing a subdivision is to go to the other side of the street from where a cable system currently exists, prepare a whole new system and then abandon the old.

Could you elaborate on the logic of that?

MR. LABRICCIOSA:  There really are two main thrusts behind that decision.  One is, again, we have to work in an existing neighbourhood that is energized.  Generally, if you're working a greenfield space, you're able to go in there, slice away at the boulevard allowance, install your equipment while the houses are being developed, and no one's relying on power.

When you're into the second generation, which is what we're facing here, people live there.  So that the choice is to leave them energized while you're building the replacement system and allow you to only reserve the outage for the end when you're transferring the connection to the new -- from the old asset to the new asset.

The second thrust is really the congestion in the boulevard space.  So as time has moved on, the maybe more elaborate boulevard allowances that the cities were used to have been shrunk.

And so going in to replace an asset that has no boulevard allowance on the one side, because you're already occupying that space, requires us to go on the other side.  And in fact, it actually secures our space in the future for future rebuilds.  So now we basically have an allowance on both sides of the street.

MR. FAYE:  Okay.  And there's nothing on the other side of the street right now?  There's no gas main or --

MR. LABRICCIOSA:  Could be.

MR. FAYE:  -- water main sort of thing?

MR. LABRICCIOSA:  Could be.  Obviously, you know, some subdivisions have gas.  All of them, I suspect, have water and Bell.  So, you know, they could be on one side or on the other side.

MR. FAYE:  And of course, if your primary system is currently on one side of the street, the houses on the other side, the secondaries have to cross the street, so they're over there as well.

MR. LABRICCIOSA:  You got it.

MR. FAYE:  I'm wondering, if indeed that's a good way to go about it, to build on the other side of the street, why do you need to replace all the secondaries?  Maybe I'll back up.

Are you replacing all the secondaries?

MR. LABRICCIOSA:  No.

MR. FAYE:  You're not.  So your projects just replace the primary cable?

MR. LABRICCIOSA:  There's a combination in some, depending on how bad and deteriorated the secondaries are, dictated by the number of cable failures on the secondary systems feeding the homes.  If it warrants replacement, we will replace the secondaries.

MR. FAYE:  But would you agree that it's a fairly simple matter to replace a secondary the day it burns off, and it only takes one customer out, right?

MR. LABRICCIOSA:  Much simpler when, again, if it's in a ducted system and, you know, in contrast to primary cable, it's much simpler to replace.

MR. FAYE:  Did I just hear you say you're going to put your secondaries in duct?

MR. LABRICCIOSA:  Some do, and if we're replacing an area that does have secondary in duct, and they're bad cables, we will replace them.

MR. FAYE:  But in the case of replacing primary, you could just splice on to the existing secondaries' tails and re-energize them and not have to dig up or tunnel up to a person's meter base, right?

MR. LABRICCIOSA:  That's correct.

MR. FAYE:  Okay.  And you are planning to do that sort of thing in your projects?

MR. LABRICCIOSA:  Yes, in some of the projects, yes.

MR. FAYE:  Would you say a majority of the projects?

MR. LABRICCIOSA:  It's hard to tell without digging into the details at this point.

MR. FAYE:  But I think I heard you say that in the situations where you're going to replace the secondaries, you would have a history of burn-offs on secondaries that would justify doing that.  It wouldn't be sort of a cavalier decision?

MR. LABRICCIOSA:  That's correct.

MR. FAYE:  Okay.  Thank you.

I'm going to move a little faster here, because I think we don't want to beat this to death.

I think before we leave this direct buried subject, I would just like to turn you just to a couple of the projects.  I'm not going to go through every one, but just a couple of them.

And if you could turn up Exhibit D1, Tab 8, Schedule 8.1, page 1 of 130, and again, I'm not going to go through 130 pages here, so we'll finish quickly.

Ready to go?

MR. LABRICCIOSA:  Yes.

MR. FAYE:  Okay.  The first entry on that first page is EO7316 project number.

MR. LABRICCIOSA:  Correct.

MR. FAYE:  And have I read somewhere in the evidence that this particular project has been deferred to 2011 because of something called a city moratorium?  Does that ring a bell?

MR. LABRICCIOSA:  Well, there are projects that that occurs.  I don't know this one in particular, but if you've read it in there, I will --

MR. FAYE:  Well, subject to check, subject to check.

MR. LABRICCIOSA:  Correct.

MR. FAYE:  I've made myself a note as I was reading the evidence.

MR. LABRICCIOSA:  Correct.

MR. FAYE:  And I'm wondering, what's a city moratorium, and how does it apply to your business?

MR. LABRICCIOSA:  It's a good point that you raise.  You know, not only do we have to develop a program that deals with the conditions of our assets, we also have to execute these programs in the environment that we find ourselves in.

So in this particular case, with the example you raised, the City has -- must have gone through that area and rebuilt the roads and the boulevards and, you know, repaved the streets, done the sidewalks.  And so they have a moratorium on road cuts and construction work on that street.

So while we have a project that requires work to be done, we basically have to coordinate with the City and convince them that they should lift that moratorium for us on that street.  On some occasions they do, but it's a special process we have to follow to actually get that work done.

MR. FAYE:  But if they won't lift the moratorium, you're pretty much stuck with waiting until 2011?

MR. LABRICCIOSA:  Correct.

MR. FAYE:  And if this project has been prioritized in your asset analysis to be done in 2008, I have to assume that this is a more urgent project than some that are coming in 2009, right?

MR. LABRICCIOSA:  That's correct.

MR. FAYE:  How do you propose to cope with an urgent replacement required and you can't do it for four or five years?

MR. LABRICCIOSA:  Well, generally what we would do is invite those people that say we can't go to do this work to one of the town-hall meetings where people are complaining about reliability.  They tend to get the message that we have to get this work done.

MR. FAYE:  Okay.  So there's some possibility that if you've got an urgent priority, that the City is going to give you some relief?

MR. LABRICCIOSA:  Yes.

MR. FAYE:  Okay.  Can you flip then to page 35?  And here's another chart.  This is "underground rehab projects".  And I'm looking particularly at those that involve St. Clair Avenue.  I'm just adding quickly -- I've got about $4.5-million in projects on this list that refer to St. Clair.

What I'd like to ask you is, why are you burying the conductor on St. Clair?  Is it on poles right now?  And if it is, why are you burying it?

MR. LABRICCIOSA:  In answer to your question, yes, it was an overhead location, and the reason for burying it is the work of the TTC to reconstruct their transit line along St. Clair, their bus route or streetcar line along St. Clair, required the road to be widened, and in order to widen the road, we had to relocate our plant, and given the movement of the relocation, we either required the poles to be in front of people's buildings or underground.

MR. FAYE:  And is the widening symmetrical on both sides, or is it widened on one side and not the other?

MR. LABRICCIOSA:  It could be on both, depending on the run.  I mean, that run is extensive from Yonge Street to, I think, Gunn's Road in the west end.

MR. FAYE:  All right.  Thanks.  I won't belabour it.  I was just curious as to why that kind of money had to go into a project like that.

And could you just comment on who pays?

MR. LABRICCIOSA:  I'm sorry?

MR. FAYE:  Excuse me.  Could you comment on who pays for that kind of project where you're being forced to do it?  You would rather not, maybe, but someone is telling you, you have to do it?

MR. LABRICCIOSA:  I'm going to reference you, in terms of the -- the economic contribution or the financial contributions to projects like that, to the Public Service Works on Highways Act, R.S.O. 1990, Chapter 49, which dictates the formulaic expression used by each party to determine who pays for what.

MR. FAYE:  Who does pay?

MR. LABRICCIOSA:  Well, Toronto Hydro has a financial obligation to pay in that road-widening, to move its work.  And the City does pay its contribution for the work that they drive as well.

MR. FAYE:  All right.  And that contribution in round figures or percentages, can you give the Panel an idea of how much that is?

MR. LABRICCIOSA:  It generally comes out to 50 percent contribution.

MR. FAYE:  Fifty percent.  And is that figure reflected as some sort of an offset to the project costs in the evidence?

MR. LABRICCIOSA:  It's a capital contribution, yes.

MR. FAYE:  Okay.  Good.

Can I turn you to page 83?

MR. LABRICCIOSA:  Yes.

MR. FAYE:  There was an IR on this, and I'll just mention it so that the Panel understands.

Two projects that appear to be identical here, both the same amount of money, and if you look at the write-up, about the same number of switches, are actually two separate projects of the same quantity of switches in two parties of their system.  That's why they're identical. They're not a duplicate.

But what I'm interested in is EO8232, equipment nomenclature enhancement east.  I guess my first question is, what is that?

MR. LABRICCIOSA:  The nomenclature project stems from work that we're carrying on as part of our amalgamation.

You can appreciate each of the six utilities labelled their equipment using a labelling system or a nomenclature system unique to their own areas.

Given the fact that we've amalgamated, we have undertaken a project to basically standardize the nomenclature.  This is really driven by safety and consistency in our organization.

You have to eliminate the possibilities of duplicate nomenclature as part of the amalgamation, and you also have to come back to a homogeneous methodology of labelling your equipment, so there is no confusion as to when someone goes out to switch a system or isolate a piece of cable, that there is no confusion of how you label it and where you apply your protection.

MR. FAYE:  Okay.  Thanks.  A very good explanation.

My question, I guess, is, in the context of cables that are failing, customers that are out of service, where does this one fit in the priority order of that sort of thing?  Is this a really urgent sort of project?

MR. LABRICCIOSA:  The priority is high enough that it belongs in the first part of this rate filing.  I don't have the assessment right in front of me that tells you, in a hierarchical sense, relative to the project above and below it, where.

MR. FAYE:  But the consequence of not doing it, if I understand you, are people might open the wrong switch and interrupt customers that shouldn't have been interrupted.  That's the sort of mistake that can occur?

MR. LABRICCIOSA:  That's correct.

MR. FAYE:  And if you would just like to remind me, when did Toronto Hydro and the other municipalities amalgamate?

MR. LABRICCIOSA:  November of 1988, I believe -- 1998.

MS. DAVIDSON:  1998.

MR. FAYE:  So we're closing in on ten years.  You've been living with this separate sort of nomenclature, maybe conflicting nomenclature, and if the Board, for instance, just said, "Well, we can't give you the money you're looking for," is this the kind of project that you would scale back or defer?

MR. LABRICCIOSA:  Again, without knowing where it sits relative to the projects above and below it, I can't really comment on is this one I would scale back or not.  We'd have to analyze that.

But I will maybe make a comment to your point around, you know, it's almost ten years after the fact.  I just mentioned to you that we're just completing our amalgamation of information systems, from a mapping perspective.  This project ties into that project quite nicely in a sense that we have to standardize on one methodology to label everything, and that took a while to sort through, as well as the systems and all the pieces of data that go with it.

So, you know, while it may seem a bit late or lax in terms of getting this done, there was a sequence in order to get to this stage where we're at.  And it's not that it's not important, it's not that we let it go.  Other work had to go ahead of it, before we can get to this stage.

MR. FAYE:  If I could flip you, then, to page

106.

MR. LABRICCIOSA:  Yes.

MR. FAYE:  This project, number 08144, is to replace 50 network transformers, at an estimated cost of $5-million.  If I divide one by the other, it seems to me each one of those network transformers on average would cost $100,000 to replace.

MR. LABRICCIOSA:  That's correct.

MR. FAYE:  If I could turn you back for a moment to the Kinectrics report, page 7, in the middle of that table I see network transformers, protectors, 85,000 each.

MR. LABRICCIOSA:  Yes.

MR. FAYE:  So there's a possibly 15 to 17 percent variance between the Kinectrics estimates and the estimate that's gone to make up this $5-million figure.  Could you comment on why this would be 15 percent more?

MR. LABRICCIOSA:  In some cases the replacement requires rewiring of the vault.  It also may require some civil work inside the vault.  So what we found, going forward, that it's convenient while you have the outage or while you're working in that vault to take on those repairs while you're there.

MR. FAYE:  Were you saying that in estimating this project, and all of this projects for that matter, that you have a detailed estimate sheet for each one of these?  It isn't just a sort of rule of thumb estimate?

MR. LABRICCIOSA:  There is an actual estimate for this particular project, yes.

MR. FAYE:  Someone would have gone out --

MR. LABRICCIOSA:  There's a location, it tells you where it is, what work you're doing.

MR. FAYE:  Very good.

MR. LABRICCIOSA:  The fact that we put it in this portfolio and aggregate it like this just tells you that, you know, we've looked at it as a portfolio, but there are locations for these.  I think there's a map somewhere in the filing that shows you where they're at.

MR. FAYE:  And if you went directly to the project file, you would find detailed estimate sheets in there that says it's going to take so much manpower, so much material?

MR. LABRICCIOSA:  That's correct.

MR. FAYE:  Someone's gone to that trouble?

MR. LABRICCIOSA:  Yes.

MR. FAYE:  Good.  And while we're still on the

Kinectrics table, could you look at note number 6, at the bottom of that table:

"Replacement costs provided may be maximum values rather than average values."

I'm wondering if you could comment on that.

MR. LABRICCIOSA:  I think in some cases, like stations, buildings, when you look at that figure, it is an estimate, and it's probably a high ballpark estimate in that whole table.

MR. FAYE:  So it doesn't mean that all of these unit prices are the maximum unit prices you ever incurred?

MR. LABRICCIOSA:  No.  When you look at things like stations, buildings, we don't repair those things every year.  We don’t replace station buildings or build them every year.  It's very infrequent.  So we might have take a rough cut at something like that.

Of course, something like the network protectors, we do that every year.  I'm fairly certain of some of those costs.

MR. FAYE:  And while we're still on this statement, can we look at underground ATS switches?  What are they?

MR. LABRICCIOSA:  Underground automatic transfer switches.

MR. FAYE:  Okay.  And they are on your network, and it looks like they cost $19,428 to replace.

MR. LABRICCIOSA:  That's a number that's in the ACA; that is correct.

MR. FAYE:  Could you turn to page 108?  This is a project number NO8148.  It appears to be to replace five automatic transfer switches, but the estimate is 654,000.

I wonder if you could explain why, if each one only costs 20, how we would get to 654 for five of them.

MR. LABRICCIOSA:  In this particular case, they're replacing the ATSs using stand-alone protector configuration, so it's changing the design.  So it's not a one for one replacement, it's an actual reconfiguration of that arrangement.

MR. FAYE:  And the actual unit itself, is it a comparable unit to an automatic transfer switch?

MR. LABRICCIOSA:  No, it isn't.

R. FAYE:  Could you describe the difference?  Without getting into too many technicalities, why would it be such a more expensive unit?

MR. LABRICCIOSA:  I'm going to give it a shot at trying to stay high enough that it makes sense but doesn't diminish the answer.

When you look at ATSs, they are really primary switches.  When you look at stand-alone protectors, they're really secondary devices.  So we're reconfiguring that system from a selective primary arrangement into a secondary type arrangement.  So they're a different-rated equipment, a different-rated component.

MR. FAYE:  Okay.  I think that's all I have on the direct buried section.  And I certainly don't have near as much on the next section, so we'll move along.  We'll see how far we can get.

MR. SOMMERVILLE:  If you're not going to complete the section, I think we're better to take it up on Monday morning, rather than break it somewhere in the middle.

MR. FAYE:  I think I can complete the section on underground rehabilitation.  It's not nearly as detailed.

MR. SOMMERVILLE:  Okay.

MR. FAYE:  So we're turning back now to our road-map sheet here, and that is D1, Tab 7, Schedule 1, page 10.  That's our summary of capital.  And the second category down is "underground rehabilitation."

And as I understand it, the distinction between this and the category we've just spent so much time on is that this stuff is all in duct work already.

MR. LABRICCIOSA:  That's correct.

MR. FAYE:  Am I right there?  Okay.  Looking at the PILC -- that's paper-insulated, lead-covered, I think is the correct terminology?

MR. LABRICCIOSA:  That's correct.

MR. FAYE:  The replacement criteria appears to be based on the number of failures per unit length of installation and the age of the cable circuit.  Is that an accurate understanding?

MR. LABRICCIOSA:  I don't know where you are drawing that conclusion from, but I would say that's one of the factors.  Another could be leaking cables, leaking splices.

MR. FAYE:  So you might have data on how many breaks you have in the lead cover that's letting out some of the insulating oil; is that --

MR. LABRICCIOSA:  That's correct.

MR. FAYE:  Okay.  But in general, once again, in the same context as the direct buried, it seems that most of the information is age-related, and the number of failures per unit is what we're relying on, on these ones.  Is that a fairly accurate statement?

MR. LABRICCIOSA:  Yes.

MR. FAYE:  Okay.  So all of our discussion around diagnostic testing, forensic testing of cables, would apply to the PILC as well, would it?

MR. LABRICCIOSA:  It is a different type of cable than cross-linked, so it's not identical, but the same sort of theories apply.

MR. FAYE:  All right.  We seem to have established that most of this cable was in duct work.  It's not direct buried cable.

MR. LABRICCIOSA:  That's correct.

MR. FAYE:  Is it reasonable, then, that this could be replaced in sections, rather than the wholesale replacement of an entire circuit?

MR. LABRICCIOSA:  It is very reasonable, only when, again, a section of cable is bad, you can actually break it down and replace it.

MR. FAYE:  And in order to understand whether that section is good or bad, we sort of have to go to diagnostic testing; is that right?

MR. LABRICCIOSA:  Or inspect it again.  If the whole cable section is leaking from the start of the feeder to the end, different parts and pieces along the way, we're likely to replace it.

MR. FAYE:  Okay.  There's various references in the evidence to this statement that it's always cheaper to repair than replace, as long as there's some -- there's no real reliability concerns.  Have I got that summarized about right?

MR. LABRICCIOSA:  I'm not sure where you're referencing that statement, but --

MR. FAYE:  It's mentioned in the Kinectrics study.  It's mentioned in your own capital --

MR. LABRICCIOSA:  In general.

MR. FAYE:  Subject to check.

MR. LABRICCIOSA:  Sure.  If you can repair it, we will.

MR. FAYE:  And one of the recommendations, I think, from the density report, was that rather than wiping more lead and solder into these cracks in the cable, that there might be other technologies, and you've referred to them as heat-shrink.

MR. LABRICCIOSA:  That's correct.

MR. FAYE:  So it is practical to withdraw a section of your lead-covered cable from the duct, put a heat-shrink patch on it, more like something like patching a bicycle tire, I imagine, and then pulling it back in again?

MR. LABRICCIOSA:  I don't think we would necessarily pull it out and push it back in.  I think what we would do is, inside a chamber, cable chamber, you know, if we saw a leaking section of cable or a leaking splice, again, as a temporary means to keep the cable in service and prolong its life, we would put heat-shrink over top of it, as you say, patch it like a bicycle tire in that respect.

MR. FAYE:  Okay.  And so I gather from that that most of the problems that you can identify happen in these splice chambers, where you can actually see the thing?

MR. LABRICCIOSA:  Yes.

MR. FAYE:  Not halfway down this duct.

MR. LABRICCIOSA:  No.

MR. FAYE:  Okay.  Good.  I'm going make you a quote out of the Kinectrics report, and ask you to take it subject to check.  I think I've transposed it properly here.  It's from page 27.  And Kinectrics says:

"It is important to distinguish between condition-related and non-condition-related cable failures."

And they mention third-party damage to your system is one of these things that is non-condition.  And I wonder if you have statistics, both on direct buried and on cable and duct, how many times does a third party damage your system?

MR. LABRICCIOSA:  We do keep data.  I just don't have it handy in front of me, in terms of how many external parties interfere with our equipment, dig-ins or damages to our cable.

MR. FAYE:  Do you have a sense of, in percentage terms, percent of failures that would be caused by third-party damage?

MR. LABRICCIOSA:  I don't.  It's -- it's relatively small, in contrast to the number of condition-based failures.

MR. FAYE:  If we took, though, all of the non-condition-related things, and then we tossed into that bucket as well all of the accessory failures, splices, elbows, things of that nature that cause you to have a customer outage, of course, but don't necessarily cause the cable to be evaluated as failed, throw all those into it, and again, as a percentage of your outages, do you have a feel for how many of those there would be as compared to true cable faults as a result of water getting in or whatever, corrosion?

MR. LABRICCIOSA:  I would say condition of the cable is a predominant failure-mode.  The other elements are all less than that.  I don't -- you have to excuse me.  I don't actually have all of the numbers in front of me, so it's pretty hard for me to focus in on any particular number.  I know that the condition is the predominant mechanism of failure.

MR. FAYE:  But you would agree there's a wide band of latitude.  You could go everywhere from 51 percent upwards on that on.  So it could be half of them?

MR. LABRICCIOSA:  I would agree.

MR. FAYE:  And the other half could be accessories and dig-ins and other third-party damage.  It could be as bad as that.

MR. LABRICCIOSA:  I agree.  It could vary.  I don't think it's quite as bad.

MR. FAYE:  Okay.  I think that's all my questions on that category, and the next category we can start next day.

MR. SOMMERVILLE:  Thank you very much.  Thank you very much, panel.  It's been a long day for you, and there's a little bit left for Monday morning, just to start the week off right.

We'll adjourn now, to resume on Monday morning at 9:30.  We'll conclude with this panel on Monday, and then start panel 7.  And --

MR. RODGER:  Panel 5.

MR. SOMMERVILLE:  I beg your pardon, panel 5, dealing with OMA&G, except for the shared services and compensation issues.

Are there any matters before we close today?  Thank you very much.

--- Whereupon the hearing adjourned at 4:46 p.m.